## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 3 | 4 | 22 | 19 | 42.4 | 8.98 | 50 | 69 | 11.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 3 | 6 | 20 | 13 | 88.2 | 20.87 | 50 | 69 | 11.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 4 | 19 | 19 | 13 | 49.6 | 0.49 | 50 | 69 | 11.6 | 67.9 | 12 | 215.4 | 228.5 | 215.4 | YES
2 | OK | 4 | 23 | 1 | 6 | 50.2 | 8.49 | 50 | 69 | 11.6 | 49.5 | 17.7 | 217.4 | 228 | 217.4 | YES
3 | OK | 6 | 5 | 5 | 19 | 94.1 | 0.24 | 50 | 69 | 11.6 | 68.4 | 11.8 | 215.5 | 228.5 | 215.5 | YES
4 | OK | 6 | 7 | 20 | 13 | 88.2 | 4.29 | 50 | 69 | 11.6 | 59.1 | 14.7 | 216.5 | 227.7 | 216.5 | YES
5 | OK | 6 | 24 | 24 | 0 | 90 | 16.34 | 50 | 69 | 11.6 | 31 | 23.6 | 222.8 | 221.1 | 221.1 | YES
6 | OK | 23 | 0 | 1 | 6 | 50.2 | 7.8 | 50 | 69 | 11.6 | 51.1 | 17.2 | 217.4 | 228 | 217.4 | YES
7 | OK | 7 | 20 | 20 | 13 | 88.2 | 3.56 | 50 | 69 | 11.6 | 60.8 | 14.2 | 216.5 | 227.7 | 216.5 | YES
8 | OK | 24 | 25 | 25 | 1 | 90.6 | 15.27 | 50 | 69 | 11.6 | 33.4 | 22.7 | 222.8 | 222.8 | 222.8 | YES
9 | OK | 0 | 1 | 1 | 6 | 50.2 | 4.47 | 50 | 69 | 11.6 | 58.7 | 14.8 | 216.5 | 228.4 | 216.5 | YES
10 | OK | 0 | 2 | 29 | 0 | 54.5 | 0.32 | 50 | 69 | 11.6 | 61.3 | 11.8 | 216.3 | 228.5 | 216.3 | YES
11 | OK | 25 | 8 | 8 | 6 | 90.8 | 14.37 | 50 | 69 | 11.6 | 35.5 | 22.1 | 222.8 | 223.1 | 222.8 | YES
12 | OK | 1 | 11 | 11 | 6 | 57.1 | 4.42 | 50 | 69 | 11.6 | 58.8 | 14.8 | 216.5 | 228.4 | 216.5 | YES
13 | OK | 2 | 29 | 29 | 0 | 54.5 | 0.25 | 50 | 69 | 11.6 | 68.4 | 11.6 | 215.4 | 228.5 | 215.4 | YES
14 | OK | 8 | 9 | 9 | 6 | 94.8 | 13.99 | 50 | 69 | 11.6 | 36.4 | 21.8 | 222.8 | 223.7 | 222.8 | YES
15 | OK | 11 | 26 | 12 | 12 | 61.5 | 2.33 | 50 | 69 | 11.6 | 63.6 | 11.8 | 215.7 | 228.5 | 215.7 | YES
16 | OK | 29 | 30 | 30 | 0 | 55 | 0.1 | 50 | 69 | 11.6 | 68.8 | 11.6 | 215.4 | 228.5 | 215.4 | YES
17 | OK | 9 | 10 | 15 | 12 | 94.9 | 13.99 | 50 | 69 | 11.6 | 36.4 | 14.3 | 222.8 | 225.9 | 222.8 | YES
18 | OK | 26 | 27 | 12 | 12 | 61.5 | 2.07 | 50 | 69 | 11.6 | 64.2 | 11.6 | 215.7 | 228.5 | 215.7 | YES
19 | ** OPTIMAL ** | 10 | 13 | 15 | 12 | 94.9 | 12.38 | 50 | 69 | 11.6 | 40.1 | 13.6 | 222.8 | 227 | 222.8 | YES
20 | OK | 27 | 28 | 12 | 12 | 61.5 | 2.07 | 50 | 69 | 11.6 | 64.2 | 11.6 | 215.7 | 228.5 | 215.7 | YES
21 | OK | 13 | 14 | 15 | 12 | 94.9 | 8.7 | 50 | 69 | 11.6 | 48.6 | 13 | 219.9 | 227.9 | 219.9 | YES
22 | OK | 28 | 12 | 12 | 12 | 61.5 | 0.65 | 50 | 69 | 11.6 | 67.5 | 11.6 | 215.7 | 228.5 | 215.7 | YES
23 | OK | 14 | 15 | 15 | 12 | 94.9 | 7.5 | 50 | 69 | 11.6 | 51.5 | 13 | 218.1 | 227.9 | 218.1 | YES
24 | OK | 15 | 16 | 16 | 24 | 96.4 | 5.55 | 50 | 69 | 11.6 | 56 | 11.6 | 218.2 | 228.5 | 218.2 | YES
25 | OK | 16 | 17 | 17 | 24 | 97.1 | 5.55 | 50 | 69 | 11.6 | 56 | 11.6 | 218.2 | 228.5 | 218.2 | YES
26 | OK | 17 | 18 | 18 | 24 | 132.2 | 3.14 | 50 | 69 | 11.6 | 61.5 | 13.9 | 218.8 | 226.4 | 218.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 00-058500
TR_B (available) | 37-013843
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 69
TR_B Baseline Loading% | 11.6
Total Scenarios Evaluated | 28
Feasible Scenarios | 26
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 13
Tie Node (TR_A side) | 15
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 94.9
Load Transferred (kW) | 12.38
TR_A Loading After (%) | 40.1
TR_B Loading After (%) | 13.6
Minimum Voltage (V) | 222.8