## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 3 | 4 | 19 | 3 | 25.6 | 8.98 | 50 | 69 | 12.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 3 | 6 | 20 | 2 | 49.3 | 20.87 | 50 | 69 | 12.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 4 | 19 | 19 | 3 | 25.6 | 0.49 | 50 | 69 | 12.4 | 67.9 | 12.7 | 215.4 | 225.6 | 215.4 | YES
2 | OK | 4 | 23 | 23 | 3 | 63.7 | 8.49 | 50 | 69 | 12.4 | 49.5 | 18.5 | 217.4 | 222.5 | 217.4 | YES
3 | OK | 6 | 5 | 5 | 3 | 79.8 | 0.24 | 50 | 69 | 12.4 | 68.4 | 12.6 | 215.5 | 225.6 | 215.5 | YES
4 | OK | 6 | 7 | 20 | 2 | 49.3 | 4.29 | 50 | 69 | 12.4 | 59.1 | 15.5 | 216.5 | 224.5 | 216.5 | YES
5 | OK | 6 | 24 | 24 | 3 | 97.9 | 16.34 | 50 | 69 | 12.4 | 31 | 24.4 | 222.8 | 217.1 | 217.1 | YES
6 | ** OPTIMAL ** | 23 | 0 | 30 | 3 | 71.8 | 7.8 | 50 | 69 | 12.4 | 51.1 | 18 | 217.4 | 222.2 | 217.4 | YES
7 | OK | 7 | 20 | 20 | 2 | 49.3 | 3.56 | 50 | 69 | 12.4 | 60.8 | 14.9 | 216.5 | 224.5 | 216.5 | YES
8 | OK | 24 | 25 | 25 | 3 | 123.8 | 15.27 | 50 | 69 | 12.4 | 33.4 | 23.6 | 222.8 | 217 | 217 | YES
9 | OK | 0 | 1 | 1 | 3 | 142.5 | 4.47 | 50 | 69 | 12.4 | 58.7 | 15.6 | 216.5 | 223.7 | 216.5 | YES
10 | OK | 0 | 2 | 30 | 3 | 71.8 | 0.32 | 50 | 69 | 12.4 | 61.3 | 12.6 | 216.3 | 225.6 | 216.3 | YES
11 | OK | 25 | 8 | 8 | 3 | 146.1 | 14.37 | 50 | 69 | 12.4 | 35.5 | 22.9 | 222.8 | 217 | 217 | YES
12 | OK | 2 | 29 | 30 | 3 | 71.8 | 0.25 | 50 | 69 | 12.4 | 68.4 | 12.4 | 215.4 | 225.6 | 215.4 | YES
13 | OK | 29 | 30 | 30 | 3 | 71.8 | 0.1 | 50 | 69 | 12.4 | 68.8 | 12.4 | 215.4 | 225.6 | 215.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 00-058500
TR_B (available) | 45-034163
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 69
TR_B Baseline Loading% | 12.4
Total Scenarios Evaluated | 15
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 0
Tie Node (TR_A side) | 30
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 71.8
Load Transferred (kW) | 7.8
TR_A Loading After (%) | 51.1
TR_B Loading After (%) | 18
Minimum Voltage (V) | 217.4