## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 3 | 4 | 12 | 30 | 104.4 | 8.98 | 50 | 69 | 41.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 3 | 6 | 18 | 31 | 38.8 | 20.87 | 50 | 69 | 41.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 4 | 23 | 12 | 30 | 104.4 | 8.49 | 50 | 69 | 41.5 | 49.5 | 43.9 | 217.4 | 218.5 | 217.4 | YES
2 | OK | 6 | 5 | 21 | 14 | 98 | 0.24 | 50 | 69 | 41.5 | 68.4 | 41.8 | 215.5 | 220.2 | 215.5 | YES
3 | OK | 6 | 7 | 7 | 14 | 133.3 | 4.29 | 50 | 69 | 41.5 | 59.1 | 46.7 | 216.5 | 219.1 | 216.5 | YES
| NG | 6 | 24 | 18 | 31 | 38.8 | 16.34 | 50 | 69 | 41.5 | 31 | 65 | 222.8 | 180.9 | 180.9 | NO
4 | OK | 23 | 0 | 12 | 30 | 104.4 | 7.8 | 50 | 69 | 41.5 | 51.1 | 43.9 | 217.4 | 218.5 | 217.4 | YES
5 | OK | 7 | 20 | 20 | 14 | 145.9 | 3.56 | 50 | 69 | 41.5 | 60.8 | 45.8 | 216.5 | 219.1 | 216.5 | YES
| NG | 24 | 25 | 18 | 31 | 38.8 | 15.27 | 50 | 69 | 41.5 | 33.4 | 63 | 222.8 | 185.2 | 185.2 | NO
6 | OK | 0 | 1 | 12 | 30 | 104.4 | 4.47 | 50 | 69 | 41.5 | 58.7 | 42.5 | 216.5 | 220.5 | 216.5 | YES
7 | OK | 0 | 2 | 2 | 14 | 122.5 | 0.32 | 50 | 69 | 41.5 | 61.3 | 41.9 | 216.3 | 220.4 | 216.3 | YES
| NG | 25 | 8 | 18 | 31 | 38.8 | 14.37 | 50 | 69 | 41.5 | 35.5 | 61.5 | 222.8 | 188.5 | 188.5 | NO
8 | OK | 1 | 11 | 12 | 30 | 104.4 | 4.42 | 50 | 69 | 41.5 | 58.8 | 42.4 | 216.5 | 220.4 | 216.5 | YES
9 | OK | 2 | 29 | 29 | 14 | 126.9 | 0.25 | 50 | 69 | 41.5 | 68.4 | 41.5 | 215.4 | 220.4 | 215.4 | YES
| NG | 8 | 9 | 18 | 31 | 38.8 | 13.99 | 50 | 69 | 41.5 | 36.4 | 60.9 | 222.8 | 189.8 | 189.8 | NO
10 | OK | 11 | 26 | 12 | 30 | 104.4 | 2.33 | 50 | 69 | 41.5 | 63.6 | 41.8 | 215.7 | 220.4 | 215.7 | YES
11 | OK | 29 | 30 | 30 | 14 | 130.4 | 0.1 | 50 | 69 | 41.5 | 68.8 | 41.5 | 215.4 | 220.4 | 215.4 | YES
| NG | 9 | 10 | 18 | 31 | 38.8 | 13.99 | 50 | 69 | 41.5 | 36.4 | 60.9 | 222.8 | 189.8 | 189.8 | NO
12 | OK | 26 | 27 | 12 | 30 | 104.4 | 2.07 | 50 | 69 | 41.5 | 64.2 | 41.5 | 215.7 | 220.4 | 215.7 | YES
| NG | 10 | 13 | 18 | 31 | 38.8 | 12.38 | 50 | 69 | 41.5 | 40.1 | 58.3 | 222.8 | 194.8 | 194.8 | NO
13 | OK | 27 | 28 | 12 | 30 | 104.4 | 2.07 | 50 | 69 | 41.5 | 64.2 | 41.5 | 215.7 | 220.4 | 215.7 | YES
| NG | 13 | 14 | 18 | 31 | 38.8 | 8.7 | 50 | 69 | 41.5 | 48.6 | 52.8 | 219.9 | 204.9 | 204.9 | NO
14 | OK | 28 | 12 | 12 | 30 | 104.4 | 0.65 | 50 | 69 | 41.5 | 67.5 | 41.5 | 215.7 | 220.4 | 215.7 | YES
| NG | 14 | 15 | 18 | 31 | 38.8 | 7.5 | 50 | 69 | 41.5 | 51.5 | 51.1 | 218.1 | 207.9 | 207.9 | NO
15 | OK | 15 | 16 | 18 | 31 | 38.8 | 5.55 | 50 | 69 | 41.5 | 56 | 48.5 | 218.2 | 212.4 | 212.4 | YES
16 | OK | 16 | 17 | 18 | 31 | 38.8 | 5.55 | 50 | 69 | 41.5 | 56 | 48.5 | 218.2 | 212.4 | 212.4 | YES
17 | ** OPTIMAL ** | 17 | 18 | 18 | 31 | 38.8 | 3.14 | 50 | 69 | 41.5 | 61.5 | 45.4 | 218.8 | 217.5 | 217.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 00-058500
TR_B (available) | 50-005680
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 69
TR_B Baseline Loading% | 41.5
Total Scenarios Evaluated | 27
Feasible Scenarios | 17
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 18
Tie Node (TR_A side) | 18
Tie Node (TR_B side) | 31
Tie Line Distance (m) | 38.8
Load Transferred (kW) | 3.14
TR_A Loading After (%) | 61.5
TR_B Loading After (%) | 45.4
Minimum Voltage (V) | 217.5