## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 4 | 3 | 15 | 30 | 78.1 | 8.95 | 50 | 82.4 | 35.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 4 | 5 | 5 | 32 | 181.9 | 4.95 | 50 | 82.4 | 35.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 3 | 32 | 15 | 30 | 78.1 | 8.95 | 50 | 82.4 | 35.2 | 29.1 | 59.7 | 218 | 196.1 | 196.1 | NO
| NG | 32 | 33 | 33 | 32 | 205.5 | 0.69 | 50 | 82.4 | 35.2 | 78.2 | 37.9 | 208.8 | 221.5 | 208.8 | NO
| NG | 32 | 37 | 15 | 30 | 78.1 | 8.26 | 50 | 82.4 | 35.2 | 33.1 | 56.4 | 218 | 199.4 | 199.4 | NO
| NG | 33 | 38 | 38 | 32 | 237.1 | 0.56 | 50 | 82.4 | 35.2 | 79 | 37.4 | 208.5 | 222 | 208.5 | NO
| NG | 37 | 34 | 15 | 30 | 78.1 | 7.95 | 50 | 82.4 | 35.2 | 34.9 | 54.9 | 218 | 200.8 | 200.8 | NO
| NG | 34 | 16 | 15 | 30 | 78.1 | 7.56 | 50 | 82.4 | 35.2 | 37.1 | 54.9 | 217.4 | 200.8 | 200.8 | NO
1 | OK | 16 | 15 | 15 | 30 | 78.1 | 5.08 | 50 | 82.4 | 35.2 | 51.7 | 45.5 | 217.4 | 210 | 210 | YES
2 | OK | 16 | 18 | 18 | 32 | 105.6 | 2.48 | 50 | 82.4 | 35.2 | 67.3 | 43.8 | 213.6 | 215.5 | 213.6 | YES
3 | OK | 15 | 22 | 42 | 29 | 87.5 | 4.95 | 50 | 82.4 | 35.2 | 52.4 | 45.5 | 217.3 | 210 | 210 | YES
4 | OK | 18 | 17 | 17 | 32 | 139.8 | 2.15 | 50 | 82.4 | 35.2 | 69.3 | 42.4 | 213.6 | 216.7 | 213.6 | YES
5 | OK | 22 | 42 | 42 | 29 | 87.5 | 4.84 | 50 | 82.4 | 35.2 | 53 | 45.5 | 217.1 | 210 | 210 | YES
6 | OK | 17 | 19 | 19 | 32 | 252.8 | 1.86 | 50 | 82.4 | 35.2 | 71 | 41.2 | 212.7 | 217.9 | 212.7 | YES
| NG | 42 | 29 | 8 | 29 | 168.2 | 4.84 | 50 | 82.4 | 35.2 | 53 | 56.5 | 217.1 | 196.2 | 196.2 | NO
7 | OK | 19 | 21 | 21 | 32 | 299.3 | 1.5 | 50 | 82.4 | 35.2 | 73.2 | 39.7 | 211.7 | 219.4 | 211.7 | YES
| NG | 29 | 28 | 8 | 29 | 168.2 | 4.84 | 50 | 82.4 | 35.2 | 53 | 56.5 | 217.1 | 196.2 | 196.2 | NO
| NG | 28 | 24 | 8 | 29 | 168.2 | 4.84 | 50 | 82.4 | 35.2 | 53 | 56.5 | 217.1 | 196.2 | 196.2 | NO
8 | OK | 24 | 25 | 25 | 29 | 262.8 | 2.48 | 50 | 82.4 | 35.2 | 67.1 | 45.5 | 213.5 | 210.8 | 210.8 | YES
| NG | 24 | 8 | 8 | 29 | 168.2 | 2.18 | 50 | 82.4 | 35.2 | 69.5 | 44.2 | 206.5 | 213.4 | 206.5 | NO
9 | ** OPTIMAL ** | 25 | 26 | 26 | 29 | 289.4 | 1.45 | 50 | 82.4 | 35.2 | 73.3 | 41.1 | 213.6 | 216.5 | 213.6 | YES
| NG | 8 | 40 | 40 | 29 | 171.4 | 1.11 | 50 | 82.4 | 35.2 | 75.7 | 39.7 | 206.8 | 218.9 | 206.8 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 23-002628
TR_B (available) | 63-014452
TR_A Rated kVA | 20
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.4
TR_B Baseline Loading% | 35.2
Total Scenarios Evaluated | 22
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 25
Switch Child Node | 26
Tie Node (TR_A side) | 26
Tie Node (TR_B side) | 29
Tie Line Distance (m) | 289.4
Load Transferred (kW) | 1.45
TR_A Loading After (%) | 73.3
TR_B Loading After (%) | 41.1
Minimum Voltage (V) | 213.6