## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 1 | 24 | 39 | 13 | 3.7 | 7.14 | 50 | 86.7 | 11.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 24 | 23 | 39 | 13 | 3.7 | 6.31 | 50 | 86.7 | 11.2 | 50 | 36.9 | 212.9 | 209.3 | 209.3 | NO
1 | OK | 23 | 22 | 39 | 13 | 3.7 | 5.81 | 50 | 86.7 | 11.2 | 52.9 | 34.8 | 212.2 | 210.8 | 210.8 | YES
2 | ** OPTIMAL ** | 22 | 21 | 39 | 13 | 3.7 | 5.17 | 50 | 86.7 | 11.2 | 56.5 | 32 | 211.2 | 212.7 | 211.2 | YES
| NG | 21 | 3 | 39 | 13 | 3.7 | 3.92 | 50 | 86.7 | 11.2 | 63.7 | 26.8 | 209.3 | 216.3 | 209.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 23-011107
TR_B (available) | 50-001169
TR_A Rated kVA | 20
TR_B Rated kVA | 30
TR_A Baseline Loading% | 86.7
TR_B Baseline Loading% | 11.2
Total Scenarios Evaluated | 5
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 22
Switch Child Node | 21
Tie Node (TR_A side) | 39
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 3.7
Load Transferred (kW) | 5.17
TR_A Loading After (%) | 56.5
TR_B Loading After (%) | 32
Minimum Voltage (V) | 211.2