## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 89 | 112 | 65 | 139 | 40.5 | 26.24 | 50 | 68.5 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 112 | 51 | 65 | 139 | 40.5 | 25.36 | 50 | 68.5 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 51 | 50 | 65 | 139 | 40.5 | 25.04 | 50 | 68.5 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 50 | 59 | 65 | 139 | 40.5 | 23.43 | 50 | 68.5 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 59 | 104 | 65 | 139 | 40.5 | 22.61 | 50 | 68.5 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 104 | 19 | 65 | 139 | 40.5 | 22.61 | 50 | 68.5 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 19 | 18 | 65 | 139 | 40.5 | 22.02 | 50 | 68.5 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 18 | 17 | 65 | 139 | 40.5 | 21.83 | 50 | 68.5 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 17 | 16 | 65 | 139 | 40.5 | 21.57 | 50 | 68.5 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 16 | 15 | 65 | 139 | 40.5 | 20.11 | 50 | 68.5 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 15 | 14 | 65 | 139 | 40.5 | 20.09 | 50 | 68.5 | 36 | [5 empty] | NO | TR_B sim: not converged
| NG | 14 | 113 | 65 | 139 | 40.5 | 17.53 | 50 | 68.5 | 36 | 47.4 | 49.4 | 213 | 129.7 | 129.7 | NO
| NG | 113 | 4 | 65 | 139 | 40.5 | 17.53 | 50 | 68.5 | 36 | 47.4 | 49.1 | 213 | 131.5 | 131.5 | NO
1 | ** OPTIMAL ** | 4 | 5 | 65 | 139 | 40.5 | 1.71 | 50 | 68.5 | 36 | 66.3 | 36.9 | 211.5 | 211.6 | 211.5 | YES
2 | OK | 5 | 94 | 65 | 139 | 40.5 | 1.63 | 50 | 68.5 | 36 | 66.4 | 36.8 | 211.4 | 211.6 | 211.4 | YES
3 | OK | 94 | 93 | 65 | 139 | 40.5 | 1.63 | 50 | 68.5 | 36 | 66.4 | 36.8 | 211.4 | 211.6 | 211.4 | YES
| NG | 93 | 65 | 65 | 139 | 40.5 | 0.14 | 50 | 68.5 | 36 | 68.3 | 36.1 | 208.7 | 211.6 | 208.7 | NO
| NG | 65 | 64 | 64 | 139 | 41.8 | 0.14 | 50 | 68.5 | 36 | 68.3 | 36.1 | 208.7 | 211.6 | 208.7 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 24-006964
TR_B (available) | 29-017505
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 68.5
TR_B Baseline Loading% | 36
Total Scenarios Evaluated | 18
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 4
Switch Child Node | 5
Tie Node (TR_A side) | 65
Tie Node (TR_B side) | 139
Tie Line Distance (m) | 40.5
Load Transferred (kW) | 1.71
TR_A Loading After (%) | 66.3
TR_B Loading After (%) | 36.9
Minimum Voltage (V) | 211.5