## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 89 | 53 | 53 | 55 | 53.8 | 1.53 | 50 | 68.5 | 66.9 | 50 | 68.6 | 209.5 | 215.6 | 209.5 | NO
| NG | 90 | 115 | 115 | 55 | 55.9 | 0.27 | 50 | 68.5 | 66.9 | 68.2 | 67.2 | 208.5 | 215.9 | 208.5 | NO
| NG | 53 | 54 | 54 | 55 | 72.5 | 1.53 | 50 | 68.5 | 66.9 | 50 | 68.6 | 209.5 | 215.6 | 209.5 | NO
| NG | 105 | 9 | 114 | 60 | 0.9 | 12.02 | 50 | 68.5 | 66.9 | 54.6 | 82.3 | 209.5 | 207.1 | 207.1 | NO
| NG | 115 | 116 | 116 | 55 | 125.3 | 0.15 | 50 | 68.5 | 66.9 | 68.3 | 67 | 208.5 | 215.9 | 208.5 | NO
| NG | 54 | 62 | 62 | 55 | 76.4 | 1.53 | 50 | 68.5 | 66.9 | 50 | 68.6 | 209.5 | 215.6 | 209.5 | NO
| NG | 9 | 8 | 114 | 60 | 0.9 | 12.02 | 50 | 68.5 | 66.9 | 54.6 | 81.7 | 209.5 | 206.8 | 206.8 | NO
| NG | 38 | 37 | 46 | 9 | 30.1 | 12.37 | 50 | 68.5 | 66.9 | 53.7 | 81.9 | 209 | 211.8 | 209 | NO
| NG | 38 | 29 | 29 | 75 | 139 | 0.24 | 50 | 68.5 | 66.9 | 51.5 | 67.1 | 209.1 | 215.9 | 209.1 | NO
| NG | 50 | 52 | 52 | 55 | 69 | 1.59 | 50 | 68.5 | 66.9 | 66.7 | 68.7 | 209 | 215.8 | 209 | NO
| NG | 62 | 63 | 63 | 54 | 107.6 | 0.9 | 50 | 68.5 | 66.9 | 50.7 | 67.9 | 209.3 | 215.8 | 209.3 | NO
| NG | 8 | 76 | 24 | 83 | 4.6 | 6.76 | 50 | 68.5 | 66.9 | 60.6 | 73.1 | 208.9 | 208.2 | 208.2 | NO
| NG | 8 | 77 | 114 | 60 | 0.9 | 4.81 | 50 | 68.5 | 66.9 | 62.9 | 72.9 | 209.1 | 212.3 | 209.1 | NO
| NG | 37 | 40 | 46 | 9 | 30.1 | 11.88 | 50 | 68.5 | 66.9 | 54.3 | 81.3 | 209 | 212.7 | 209 | NO
| NG | 29 | 28 | 28 | 53 | 148.3 | 0.24 | 50 | 68.5 | 66.9 | 51.5 | 67.1 | 209.1 | 215.9 | 209.1 | NO
| NG | 52 | 66 | 66 | 55 | 95.9 | 0.94 | 50 | 68.5 | 66.9 | 67.4 | 68 | 209 | 215.8 | 209 | NO
| NG | 76 | 27 | 24 | 83 | 4.6 | 6.7 | 50 | 68.5 | 66.9 | 60.7 | 73 | 208.9 | 208.4 | 208.4 | NO
| NG | 77 | 78 | 114 | 60 | 0.9 | 4.8 | 50 | 68.5 | 66.9 | 62.9 | 72.9 | 209.1 | 212.4 | 209.1 | NO
| NG | 40 | 39 | 46 | 9 | 30.1 | 10.2 | 50 | 68.5 | 66.9 | 56.2 | 79.2 | 208.9 | 212 | 208.9 | NO
| NG | 40 | 41 | 41 | 75 | 129 | 1.68 | 50 | 68.5 | 66.9 | 66.5 | 68.2 | 208.6 | 215.7 | 208.6 | NO
| NG | 66 | 111 | 111 | 55 | 129.7 | 0.93 | 50 | 68.5 | 66.9 | 67.4 | 67.9 | 209 | 215.8 | 209 | NO
| NG | 27 | 26 | 24 | 83 | 4.6 | 5.96 | 50 | 68.5 | 66.9 | 61.6 | 73 | 208.7 | 208.4 | 208.4 | NO
| NG | 78 | 79 | 114 | 60 | 0.9 | 4.58 | 50 | 68.5 | 66.9 | 63.2 | 72.6 | 209 | 212.7 | 209 | NO
| NG | 39 | 43 | 46 | 9 | 30.1 | 9.83 | 50 | 68.5 | 66.9 | 56.6 | 78.8 | 208.8 | 211.9 | 208.8 | NO
| NG | 41 | 42 | 42 | 81 | 132.9 | 0.88 | 50 | 68.5 | 66.9 | 67.5 | 67.9 | 208.6 | 215.9 | 208.6 | NO
| NG | 26 | 71 | 24 | 83 | 4.6 | 2.97 | 50 | 68.5 | 66.9 | 65 | 70.7 | 208.5 | 210 | 208.5 | NO
| NG | 26 | 75 | 88 | 9 | 6.1 | 2.99 | 50 | 68.5 | 66.9 | 65 | 70.4 | 208.7 | 215.7 | 208.7 | NO
| NG | 79 | 80 | 114 | 60 | 0.9 | 3.07 | 50 | 68.5 | 66.9 | 64.9 | 70.7 | 209 | 212.5 | 209 | NO
| NG | 43 | 45 | 46 | 9 | 30.1 | 8.55 | 50 | 68.5 | 66.9 | 58.1 | 77.3 | 208.5 | 211.7 | 208.5 | NO
| NG | 42 | 55 | 55 | 81 | 133.4 | 0.19 | 50 | 68.5 | 66.9 | 68.3 | 66.9 | 208.5 | 216 | 208.5 | NO
| NG | 71 | 70 | 24 | 83 | 4.6 | 2.8 | 50 | 68.5 | 66.9 | 65.2 | 70.4 | 208.5 | 209.9 | 208.5 | NO
| NG | 75 | 74 | 88 | 9 | 6.1 | 2.87 | 50 | 68.5 | 66.9 | 65.1 | 70.2 | 208.7 | 215.7 | 208.7 | NO
| NG | 80 | 81 | 114 | 60 | 0.9 | 1.65 | 50 | 68.5 | 66.9 | 66.6 | 68.9 | 208.7 | 214.8 | 208.7 | NO
| NG | 45 | 44 | 46 | 9 | 30.1 | 7.72 | 50 | 68.5 | 66.9 | 59.1 | 76.3 | 208.5 | 211.3 | 208.5 | NO
| NG | 70 | 69 | 24 | 83 | 4.6 | 0.58 | 50 | 68.5 | 66.9 | 67.8 | 67.6 | 208.5 | 215 | 208.5 | NO
| NG | 74 | 73 | 88 | 9 | 6.1 | 2.78 | 50 | 68.5 | 66.9 | 65.2 | 70.1 | 208.7 | 215.7 | 208.7 | NO
| NG | 81 | 82 | 114 | 60 | 0.9 | 0.86 | 50 | 68.5 | 66.9 | 67.5 | 67.9 | 208.7 | 214.6 | 208.7 | NO
| NG | 44 | 46 | 46 | 9 | 30.1 | 7.55 | 50 | 68.5 | 66.9 | 59.3 | 76.1 | 208.4 | 211.3 | 208.4 | NO
| NG | 73 | 72 | 88 | 9 | 6.1 | 2.63 | 50 | 68.5 | 66.9 | 65.4 | 69.9 | 208.7 | 215.7 | 208.7 | NO
| NG | 82 | 68 | 114 | 60 | 0.9 | 0.4 | 50 | 68.5 | 66.9 | 68 | 67.3 | 208.6 | 215.4 | 208.6 | NO
| NG | 46 | 56 | 58 | 9 | 53.7 | 5.87 | 50 | 68.5 | 66.9 | 61.2 | 74.1 | 208.5 | 210.9 | 208.5 | NO
| NG | 72 | 21 | 88 | 9 | 6.1 | 2.33 | 50 | 68.5 | 66.9 | 65.8 | 69.6 | 208.6 | 215.8 | 208.6 | NO
| NG | 68 | 67 | 114 | 60 | 0.9 | 0.15 | 50 | 68.5 | 66.9 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 66.9% (degenerate)
| NG | 56 | 58 | 58 | 9 | 53.7 | 0.55 | 50 | 68.5 | 66.9 | 67.8 | 67.5 | 208.5 | 216 | 208.5 | NO
| NG | 56 | 97 | 97 | 9 | 66.6 | 2.88 | 50 | 68.5 | 66.9 | 64.8 | 70.3 | 208.5 | 216 | 208.5 | NO
| NG | 56 | 108 | 108 | 9 | 92.6 | 2.44 | 50 | 68.5 | 66.9 | 65.4 | 69.7 | 208.5 | 216 | 208.5 | NO
| NG | 21 | 20 | 88 | 9 | 6.1 | 2.25 | 50 | 68.5 | 66.9 | 65.8 | 69.5 | 208.6 | 215.8 | 208.6 | NO
| NG | 58 | 117 | 122 | 91 | 115.5 | 0.29 | 50 | 68.5 | 66.9 | 68.1 | 67.2 | 208.5 | 214.7 | 208.5 | NO
| NG | 97 | 47 | 47 | 9 | 91.7 | 2.88 | 50 | 68.5 | 66.9 | 64.8 | 70.3 | 208.5 | 216 | 208.5 | NO
| NG | 108 | 110 | 110 | 9 | 130.4 | 1.07 | 50 | 68.5 | 66.9 | 67.1 | 68.1 | 208.5 | 216 | 208.5 | NO
| NG | 20 | 88 | 88 | 9 | 6.1 | 2.25 | 50 | 68.5 | 66.9 | 65.8 | 69.5 | 208.6 | 215.8 | 208.6 | NO
| NG | 117 | 118 | 122 | 91 | 115.5 | 0.27 | 50 | 68.5 | 66.9 | 68.1 | 67.2 | 208.5 | 214.8 | 208.5 | NO
| NG | 47 | 48 | 48 | 9 | 111.8 | 2.25 | 50 | 68.5 | 66.9 | 65.6 | 69.5 | 208.5 | 216 | 208.5 | NO
| NG | 88 | 96 | 96 | 9 | 20.7 | 2.25 | 50 | 68.5 | 66.9 | 65.8 | 69.5 | 208.6 | 215.8 | 208.6 | NO
| NG | 118 | 119 | 122 | 91 | 115.5 | 0.01 | 50 | 68.5 | 66.9 | 68.5 | 66.9 | 208.5 | 215.9 | 208.5 | NO
| NG | 48 | 49 | 49 | 9 | 147.7 | 1.87 | 50 | 68.5 | 66.9 | 66.1 | 69.1 | 208.5 | 216 | 208.5 | NO
| NG | 96 | 95 | 22 | 18 | 35.5 | 2.03 | 50 | 68.5 | 66.9 | 66.1 | 69.4 | 208.6 | 214.1 | 208.6 | NO
| NG | 1 | 83 | 6 | 7 | 10 | 12.66 | 50 | 68.5 | 66.9 | 53.1 | 81.8 | 212.8 | 214.9 | 212.8 | NO
| NG | 95 | 99 | 22 | 18 | 35.5 | 1.44 | 50 | 68.5 | 66.9 | 66.8 | 68.7 | 208.6 | 215 | 208.6 | NO
| NG | 83 | 84 | 6 | 7 | 10 | 12.48 | 50 | 68.5 | 66.9 | 53.3 | 81.5 | 212.8 | 214.9 | 212.8 | NO
| NG | 99 | 98 | 22 | 18 | 35.5 | 0.67 | 50 | 68.5 | 66.9 | 66.8 | 67.7 | 208.6 | 214.6 | 208.6 | NO
1 | ** OPTIMAL ** | 84 | 85 | 6 | 7 | 10 | 10.29 | 50 | 68.5 | 66.9 | 55.8 | 78.9 | 212.5 | 214.9 | 212.5 | YES
| NG | 98 | 23 | 22 | 18 | 35.5 | 0.59 | 50 | 68.5 | 66.9 | 67.8 | 67.6 | 208.6 | 214.8 | 208.6 | NO
2 | OK | 85 | 86 | 6 | 7 | 10 | 9.22 | 50 | 68.5 | 66.9 | 57.1 | 77.6 | 212.3 | 214.9 | 212.3 | YES
3 | OK | 86 | 87 | 6 | 7 | 10 | 7.52 | 50 | 68.5 | 66.9 | 59.2 | 75.7 | 211.9 | 214.9 | 211.9 | YES
4 | OK | 87 | 2 | 6 | 7 | 10 | 7.52 | 50 | 68.5 | 66.9 | 59.2 | 75.5 | 211.9 | 214.9 | 211.9 | YES
5 | OK | 2 | 3 | 6 | 7 | 10 | 7.21 | 50 | 68.5 | 66.9 | 59.5 | 75.3 | 211.9 | 214.9 | 211.9 | YES
| NG | 2 | 91 | 91 | 7 | 146 | 0.2 | 50 | 68.5 | 66.9 | 68.2 | 67.1 | 208.4 | 215.9 | 208.4 | NO
6 | OK | 3 | 10 | 6 | 7 | 10 | 6.64 | 50 | 68.5 | 66.9 | 60.2 | 74.6 | 211.9 | 214.9 | 211.9 | YES
7 | OK | 10 | 7 | 6 | 7 | 10 | 5.62 | 50 | 68.5 | 66.9 | 61.4 | 73.4 | 211.9 | 215.1 | 211.9 | YES
8 | OK | 7 | 6 | 6 | 7 | 10 | 5.36 | 50 | 68.5 | 66.9 | 61.7 | 73.1 | 211.9 | 215.1 | 211.9 | YES
9 | OK | 6 | 12 | 11 | 86 | 30.8 | 2.97 | 50 | 68.5 | 66.9 | 64.7 | 67.7 | 211.9 | 215.4 | 211.9 | YES
10 | OK | 12 | 13 | 11 | 86 | 30.8 | 2.42 | 50 | 68.5 | 66.9 | 65.4 | 67.7 | 211.8 | 215.4 | 211.8 | YES
| NG | 13 | 11 | 11 | 86 | 30.8 | 0.89 | 50 | 68.5 | 66.9 | 67.4 | 67.7 | 208.2 | 215.4 | 208.2 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 24-006964
TR_B (available) | 44-005222
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 68.5
TR_B Baseline Loading% | 66.9
Total Scenarios Evaluated | 74
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 84
Switch Child Node | 85
Tie Node (TR_A side) | 6
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 10
Load Transferred (kW) | 10.29
TR_A Loading After (%) | 55.8
TR_B Loading After (%) | 78.9
Minimum Voltage (V) | 212.5