## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 24 | 51 | 11 | 71.6 | 15.64 | 50 | 88.5 | 2.4 | 26.2 | 82.5 | 223.2 | 151.6 | 151.6 | NO
| NG | 24 | 23 | 51 | 11 | 71.6 | 15.33 | 50 | 88.5 | 2.4 | 27.4 | 79.7 | 223 | 154.8 | 154.8 | NO
| NG | 23 | 22 | 51 | 11 | 71.6 | 15.09 | 50 | 88.5 | 2.4 | 28.2 | 77.7 | 223 | 157.1 | 157.1 | NO
| NG | 22 | 21 | 51 | 11 | 71.6 | 14.38 | 50 | 88.5 | 2.4 | 31 | 72.2 | 222.6 | 163.3 | 163.3 | NO
| NG | 21 | 20 | 51 | 11 | 71.6 | 14.11 | 50 | 88.5 | 2.4 | 32.1 | 70.2 | 222.6 | 165.5 | 165.5 | NO
| NG | 20 | 11 | 51 | 11 | 71.6 | 14.11 | 50 | 88.5 | 2.4 | 32.1 | 70.2 | 222.6 | 165.5 | 165.5 | NO
| NG | 11 | 10 | 51 | 11 | 71.6 | 14.11 | 50 | 88.5 | 2.4 | 32.1 | 70.2 | 222.6 | 165.5 | 165.5 | NO
| NG | 10 | 9 | 51 | 11 | 71.6 | 9.81 | 50 | 88.5 | 2.4 | 48.7 | 44.6 | 222.6 | 194.2 | 194.2 | NO
| NG | 9 | 8 | 51 | 11 | 71.6 | 8.7 | 50 | 88.5 | 2.4 | 53 | 39.1 | 222.5 | 199 | 199 | NO
| NG | 8 | 34 | 51 | 11 | 71.6 | 7.75 | 50 | 88.5 | 2.4 | 56.6 | 34.7 | 221.6 | 202.8 | 202.8 | NO
| NG | 34 | 33 | 51 | 11 | 71.6 | 7.75 | 50 | 88.5 | 2.4 | 56.6 | 34.7 | 221.6 | 202.8 | 202.8 | NO
| NG | 33 | 7 | 51 | 11 | 71.6 | 7.68 | 50 | 88.5 | 2.4 | 56.9 | 34.3 | 221.5 | 203.1 | 203.1 | NO
| NG | 7 | 6 | 51 | 11 | 71.6 | 7.68 | 50 | 88.5 | 2.4 | 56.9 | 34.3 | 221.5 | 203.1 | 203.1 | NO
| NG | 6 | 32 | 51 | 11 | 71.6 | 7.66 | 50 | 88.5 | 2.4 | 57 | 34.2 | 221.5 | 203.2 | 203.2 | NO
1 | ** OPTIMAL ** | 32 | 31 | 51 | 11 | 71.6 | 3.27 | 50 | 88.5 | 2.4 | 74.7 | 15.2 | 212.2 | 222.2 | 212.2 | YES
2 | OK | 31 | 42 | 51 | 11 | 71.6 | 3.2 | 50 | 88.5 | 2.4 | 75 | 14.9 | 212.1 | 222.4 | 212.1 | YES
3 | OK | 42 | 41 | 51 | 11 | 71.6 | 2.73 | 50 | 88.5 | 2.4 | 76.9 | 13.1 | 211.2 | 223.8 | 211.2 | YES
4 | OK | 41 | 40 | 51 | 11 | 71.6 | 2.7 | 50 | 88.5 | 2.4 | 77 | 12.9 | 211.1 | 223.9 | 211.1 | YES
5 | OK | 40 | 39 | 51 | 11 | 71.6 | 2.65 | 50 | 88.5 | 2.4 | 77.3 | 12.7 | 211 | 224.1 | 211 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 26-004055
TR_B (available) | 38-006608
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 88.5
TR_B Baseline Loading% | 2.4
Total Scenarios Evaluated | 19
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 32
Switch Child Node | 31
Tie Node (TR_A side) | 51
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 71.6
Load Transferred (kW) | 3.27
TR_A Loading After (%) | 74.7
TR_B Loading After (%) | 15.2
Minimum Voltage (V) | 212.2