## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 35 | 34 | 34 | 45 | 72.9 | 58.25 | 50 | 82.5 | 31.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 35 | 36 | 36 | 45 | 66.9 | 10.88 | 50 | 82.5 | 31.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 34 | 33 | 33 | 45 | 93.1 | 58.25 | 50 | 82.5 | 31.4 | 12.5 | 68.4 | 228.7 | 143.7 | 143.7 | NO
| NG | 36 | 37 | 37 | 45 | 67.8 | 10.88 | 50 | 82.5 | 31.4 | 70 | 36.9 | 207.4 | 207.7 | 207.4 | NO
| NG | 33 | 24 | 26 | 45 | 94.3 | 58.25 | 50 | 82.5 | 31.4 | 0 | 67.9 | 0 | 147.5 | 0 | NO
| NG | 37 | 18 | 18 | 45 | 87 | 3.53 | 50 | 82.5 | 31.4 | 78.5 | 33.1 | 206.7 | 216.9 | 206.7 | NO
| NG | 24 | 26 | 26 | 45 | 94.3 | 55.87 | 50 | 82.5 | 31.4 | [5 empty] | NO | TR_A sim: loading 10548% (degenerate)
| NG | 18 | 19 | 22 | 45 | 105.5 | 3.53 | 50 | 82.5 | 31.4 | 78.5 | 33.1 | 206.7 | 216.9 | 206.7 | NO
| NG | 26 | 27 | 27 | 45 | 100.6 | 49.73 | 50 | 82.5 | 31.4 | 22.3 | 63 | 226.9 | 143.7 | 143.7 | NO
| NG | 27 | 28 | 28 | 45 | 108.1 | 46.94 | 50 | 82.5 | 31.4 | 25.5 | 61.6 | 225.4 | 143 | 143 | NO
| NG | 28 | 30 | 30 | 45 | 136.7 | 45.81 | 50 | 82.5 | 31.4 | 26.8 | 60.4 | 225.5 | 144 | 144 | NO
| NG | 30 | 29 | 2 | 45 | 154.1 | 37.93 | 50 | 82.5 | 31.4 | 35.9 | 54.2 | 223.8 | 155.2 | 155.2 | NO
| NG | 29 | 31 | 2 | 45 | 154.1 | 35.84 | 50 | 82.5 | 31.4 | 38.4 | 53.1 | 222 | 149.9 | 149.9 | NO
| NG | 31 | 5 | 2 | 45 | 154.1 | 30.7 | 50 | 82.5 | 31.4 | 44.4 | 48.1 | 222.2 | 187.6 | 187.6 | NO
| NG | 5 | 40 | 2 | 45 | 154.1 | 21.56 | 50 | 82.5 | 31.4 | 55.3 | 43.1 | 217.8 | 185.2 | 185.2 | NO
| NG | 40 | 39 | 2 | 45 | 154.1 | 21.36 | 50 | 82.5 | 31.4 | 55.5 | 43 | 217.5 | 185 | 185 | NO
| NG | 39 | 38 | 2 | 45 | 154.1 | 20.23 | 50 | 82.5 | 31.4 | 56.9 | 42.2 | 217.6 | 190.8 | 190.8 | NO
| NG | 38 | 13 | 2 | 45 | 154.1 | 15.75 | 50 | 82.5 | 31.4 | 61.5 | 39.6 | 217.5 | 203.5 | 203.5 | NO
| NG | 38 | 14 | 41 | 45 | 173 | 3.84 | 50 | 82.5 | 31.4 | 77.6 | 33.2 | 206.8 | 216.8 | 206.8 | NO
| NG | 13 | 12 | 2 | 45 | 154.1 | 15.13 | 50 | 82.5 | 31.4 | 63 | 39.2 | 217.6 | 203.2 | 203.2 | NO
| NG | 14 | 15 | 41 | 45 | 173 | 3.42 | 50 | 82.5 | 31.4 | 78.2 | 33 | 206.2 | 216.8 | 206.2 | NO
| NG | 12 | 42 | 2 | 45 | 154.1 | 13.55 | 50 | 82.5 | 31.4 | 65 | 38.3 | 215.7 | 205.9 | 205.9 | NO
| NG | 42 | 43 | 2 | 45 | 154.1 | 13.08 | 50 | 82.5 | 31.4 | 65.6 | 38.1 | 215.1 | 205.5 | 205.5 | NO
| NG | 43 | 44 | 2 | 45 | 154.1 | 13.07 | 50 | 82.5 | 31.4 | 65.6 | 38.1 | 215.1 | 205.5 | 205.5 | NO
| NG | 44 | 45 | 2 | 45 | 154.1 | 11.21 | 50 | 82.5 | 31.4 | 67.9 | 37 | 215.3 | 209.9 | 209.9 | NO
| NG | 45 | 16 | 2 | 45 | 154.1 | 7.95 | 50 | 82.5 | 31.4 | 72.1 | 35.4 | 212 | 209 | 209 | NO
1 | OK | 16 | 0 | 3 | 45 | 171.8 | 6.43 | 50 | 82.5 | 31.4 | 73.6 | 34.6 | 211.2 | 212.3 | 211.2 | YES
2 | ** OPTIMAL ** | 0 | 1 | 3 | 45 | 171.8 | 5.52 | 50 | 82.5 | 31.4 | 75.2 | 34.1 | 211.7 | 215.2 | 211.7 | YES
| NG | 1 | 3 | 3 | 45 | 171.8 | 2.56 | 50 | 82.5 | 31.4 | 79.1 | 32.6 | 206.3 | 216.7 | 206.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 26-009238
TR_B (available) | 37-018969
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 82.5
TR_B Baseline Loading% | 31.4
Total Scenarios Evaluated | 29
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 0
Switch Child Node | 1
Tie Node (TR_A side) | 3
Tie Node (TR_B side) | 45
Tie Line Distance (m) | 171.8
Load Transferred (kW) | 5.52
TR_A Loading After (%) | 75.2
TR_B Loading After (%) | 34.1
Minimum Voltage (V) | 211.7