## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 35 | 34 | 25 | 14 | 45.3 | 58.25 | 50 | 82.5 | 19.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 35 | 36 | 46 | 14 | 5.4 | 10.88 | 95 | 82.5 | 19.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 34 | 33 | 25 | 14 | 45.3 | 58.25 | 50 | 82.5 | 19.7 | 12.5 | 95 | 228.7 | 188.6 | 188.6 | NO
| NG | 36 | 37 | 46 | 14 | 5.4 | 10.88 | 95 | 82.5 | 19.7 | 70 | 32.4 | 207.4 | 223 | 207.4 | NO
| NG | 33 | 24 | 25 | 14 | 45.3 | 58.25 | 50 | 82.5 | 19.7 | 0 | 95 | 0 | 188.6 | 0 | NO
| NG | 37 | 18 | 46 | 14 | 5.4 | 3.53 | 95 | 82.5 | 19.7 | 78.5 | 23.8 | 206.7 | 225.7 | 206.7 | NO
| NG | 24 | 26 | 26 | 14 | 76.4 | 55.87 | 50 | 82.5 | 19.7 | 202.8 | 92 | 50 | 188.8 | 50 | NO
| NG | 18 | 19 | 19 | 14 | 50.8 | 3.53 | 50 | 82.5 | 19.7 | 78.5 | 23.8 | 206.7 | 225.8 | 206.7 | NO
| NG | 26 | 27 | 27 | 14 | 106.8 | 49.73 | 50 | 82.5 | 19.7 | 22.3 | 84.7 | 226.9 | 187.1 | 187.1 | NO
| NG | 27 | 28 | 28 | 14 | 122.5 | 46.94 | 50 | 82.5 | 19.7 | 25.5 | 81.5 | 225.4 | 186 | 186 | NO
| NG | 28 | 30 | 3 | 14 | 122.9 | 45.81 | 50 | 82.5 | 19.7 | 26.8 | 80.5 | 225.5 | 176.8 | 176.8 | NO
| NG | 30 | 29 | 3 | 14 | 122.9 | 37.93 | 50 | 82.5 | 19.7 | 35.9 | 68 | 223.8 | 191.5 | 191.5 | NO
| NG | 29 | 31 | 3 | 14 | 122.9 | 35.84 | 50 | 82.5 | 19.7 | 38.4 | 65.2 | 222 | 189.8 | 189.8 | NO
| NG | 31 | 5 | 3 | 14 | 122.9 | 30.7 | 50 | 82.5 | 19.7 | 44.4 | 57.3 | 222.2 | 205.7 | 205.7 | NO
| NG | 5 | 40 | 3 | 14 | 122.9 | 21.56 | 50 | 82.5 | 19.7 | 55.3 | 46.1 | 217.8 | 204.7 | 204.7 | NO
| NG | 40 | 39 | 3 | 14 | 122.9 | 21.36 | 50 | 82.5 | 19.7 | 55.5 | 45.9 | 217.5 | 204.5 | 204.5 | NO
| NG | 39 | 38 | 3 | 14 | 122.9 | 20.23 | 50 | 82.5 | 19.7 | 56.9 | 44.3 | 217.6 | 207.6 | 207.6 | NO
1 | OK | 38 | 13 | 3 | 14 | 122.9 | 15.75 | 50 | 82.5 | 19.7 | 61.5 | 38.6 | 217.5 | 215.8 | 215.8 | YES
2 | ** OPTIMAL ** | 13 | 12 | 3 | 14 | 122.9 | 15.13 | 50 | 82.5 | 19.7 | 63 | 37.8 | 217.6 | 217.2 | 217.2 | YES
3 | OK | 12 | 42 | 3 | 14 | 122.9 | 13.55 | 50 | 82.5 | 19.7 | 65 | 35.9 | 215.7 | 216.4 | 215.7 | YES
4 | OK | 42 | 43 | 3 | 14 | 122.9 | 13.08 | 50 | 82.5 | 19.7 | 65.6 | 35.3 | 215.1 | 216.1 | 215.1 | YES
5 | OK | 43 | 44 | 3 | 14 | 122.9 | 13.07 | 50 | 82.5 | 19.7 | 65.6 | 35.3 | 215.1 | 216.1 | 215.1 | YES
6 | OK | 44 | 45 | 3 | 14 | 122.9 | 11.21 | 50 | 82.5 | 19.7 | 67.9 | 32.9 | 215.3 | 220 | 215.3 | YES
7 | OK | 45 | 16 | 3 | 14 | 122.9 | 7.95 | 50 | 82.5 | 19.7 | 72.1 | 29 | 212 | 222.2 | 212 | YES
8 | OK | 16 | 0 | 3 | 14 | 122.9 | 6.43 | 50 | 82.5 | 19.7 | 73.6 | 27.2 | 211.2 | 224 | 211.2 | YES
9 | OK | 0 | 1 | 3 | 14 | 122.9 | 5.52 | 50 | 82.5 | 19.7 | 75.2 | 26.1 | 211.7 | 225.5 | 211.7 | YES
| NG | 1 | 3 | 3 | 14 | 122.9 | 2.56 | 50 | 82.5 | 19.7 | 79.1 | 22.7 | 206.3 | 225 | 206.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 26-009238
TR_B (available) | 63-029879
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 82.5
TR_B Baseline Loading% | 19.7
Total Scenarios Evaluated | 27
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 13
Switch Child Node | 12
Tie Node (TR_A side) | 3
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 122.9
Load Transferred (kW) | 15.13
TR_A Loading After (%) | 63
TR_B Loading After (%) | 37.8
Minimum Voltage (V) | 217.2