## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 35 | 34 | 32 | 52 | 26.5 | 58.25 | 50 | 82.5 | 38.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 35 | 36 | 23 | 85 | 140.4 | 10.88 | 50 | 82.5 | 38.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 34 | 33 | 32 | 52 | 26.5 | 58.25 | 50 | 82.5 | 38.2 | 12.5 | 70.9 | 228.7 | 178.6 | 178.6 | NO
| NG | 36 | 37 | 23 | 85 | 140.4 | 10.88 | 50 | 82.5 | 38.2 | 70 | 39.8 | 207.4 | 212.6 | 207.4 | NO
| NG | 33 | 24 | 32 | 52 | 26.5 | 58.25 | 50 | 82.5 | 38.2 | 0 | 70.9 | 0 | 178.6 | 0 | NO
| NG | 37 | 18 | 23 | 85 | 140.4 | 3.53 | 50 | 82.5 | 38.2 | 78.5 | 39.8 | 206.7 | 212.6 | 206.7 | NO
| NG | 24 | 26 | 32 | 52 | 26.5 | 55.87 | 50 | 82.5 | 38.2 | [5 empty] | NO | TR_A sim: loading 10548% (degenerate)
| NG | 18 | 19 | 23 | 85 | 140.4 | 3.53 | 50 | 82.5 | 38.2 | 78.5 | 39.8 | 206.7 | 212.6 | 206.7 | NO
| NG | 26 | 27 | 32 | 52 | 26.5 | 49.73 | 50 | 82.5 | 38.2 | 22.3 | 66 | 226.9 | 177 | 177 | NO
| NG | 27 | 28 | 32 | 52 | 26.5 | 46.94 | 50 | 82.5 | 38.2 | 25.5 | 64.7 | 225.4 | 176.7 | 176.7 | NO
| NG | 28 | 30 | 32 | 52 | 26.5 | 45.81 | 50 | 82.5 | 38.2 | 26.8 | 63.8 | 225.5 | 180.2 | 180.2 | NO
| NG | 30 | 29 | 32 | 52 | 26.5 | 37.93 | 50 | 82.5 | 38.2 | 35.9 | 59.1 | 223.8 | 176.1 | 176.1 | NO
| NG | 29 | 31 | 32 | 52 | 26.5 | 35.84 | 50 | 82.5 | 38.2 | 38.4 | 58.1 | 222 | 174.7 | 174.7 | NO
| NG | 31 | 5 | 32 | 52 | 26.5 | 30.7 | 50 | 82.5 | 38.2 | 44.4 | 54.4 | 222.2 | 189.1 | 189.1 | NO
| NG | 5 | 4 | 32 | 52 | 26.5 | 9.14 | 50 | 82.5 | 38.2 | 71.4 | 42.7 | 206.9 | 212.6 | 206.9 | NO
| NG | 5 | 40 | 11 | 41 | 63.9 | 21.56 | 50 | 82.5 | 38.2 | 55.3 | 49.4 | 217.8 | 199.1 | 199.1 | NO
| NG | 4 | 6 | 32 | 52 | 26.5 | 6.82 | 50 | 82.5 | 38.2 | 74 | 41.5 | 207.1 | 212.6 | 207.1 | NO
| NG | 40 | 39 | 11 | 41 | 63.9 | 21.36 | 50 | 82.5 | 38.2 | 55.5 | 49.3 | 217.5 | 199 | 199 | NO
| NG | 6 | 7 | 32 | 52 | 26.5 | 4.11 | 50 | 82.5 | 38.2 | 77.3 | 40.2 | 207.5 | 212.4 | 207.5 | NO
| NG | 39 | 38 | 11 | 41 | 63.9 | 20.23 | 50 | 82.5 | 38.2 | 56.9 | 48.6 | 217.6 | 200.9 | 200.9 | NO
| NG | 38 | 13 | 11 | 41 | 63.9 | 15.75 | 50 | 82.5 | 38.2 | 61.5 | 46.2 | 217.5 | 205.8 | 205.8 | NO
| NG | 38 | 14 | 14 | 41 | 90.4 | 3.84 | 50 | 82.5 | 38.2 | 77.6 | 40.1 | 206.8 | 211.5 | 206.8 | NO
| NG | 13 | 12 | 11 | 41 | 63.9 | 15.13 | 50 | 82.5 | 38.2 | 63 | 45.8 | 217.6 | 206.7 | 206.7 | NO
| NG | 14 | 15 | 41 | 85 | 102.9 | 3.42 | 50 | 82.5 | 38.2 | 78.2 | 38.6 | 206.2 | 212.5 | 206.2 | NO
1 | OK | 12 | 42 | 44 | 81 | 73.4 | 13.55 | 50 | 82.5 | 38.2 | 65 | 38.2 | 215.7 | 212.5 | 212.5 | YES
2 | OK | 42 | 43 | 44 | 81 | 73.4 | 13.08 | 50 | 82.5 | 38.2 | 65.6 | 38.2 | 215.1 | 212.5 | 212.5 | YES
3 | OK | 43 | 44 | 44 | 81 | 73.4 | 13.07 | 50 | 82.5 | 38.2 | 65.6 | 38.2 | 215.1 | 212.5 | 212.5 | YES
4 | ** OPTIMAL ** | 44 | 45 | 45 | 85 | 74.3 | 11.21 | 50 | 82.5 | 38.2 | 67.9 | 38.2 | 215.3 | 212.5 | 212.5 | YES
5 | OK | 45 | 16 | 16 | 85 | 78.3 | 7.95 | 50 | 82.5 | 38.2 | 72.1 | 38.2 | 212 | 212.5 | 212 | YES
6 | OK | 16 | 0 | 0 | 85 | 79.6 | 6.43 | 50 | 82.5 | 38.2 | 73.6 | 38.2 | 211.2 | 212.5 | 211.2 | YES
7 | OK | 0 | 1 | 1 | 85 | 87.4 | 5.52 | 50 | 82.5 | 38.2 | 75.2 | 38.2 | 211.7 | 212.5 | 211.7 | YES
| NG | 1 | 3 | 3 | 85 | 102.5 | 2.56 | 50 | 82.5 | 38.2 | 79.1 | 38.2 | 206.3 | 212.5 | 206.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 26-009238
TR_B (available) | 66-025633
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 82.5
TR_B Baseline Loading% | 38.2
Total Scenarios Evaluated | 32
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 44
Switch Child Node | 45
Tie Node (TR_A side) | 45
Tie Node (TR_B side) | 85
Tie Line Distance (m) | 74.3
Load Transferred (kW) | 11.21
TR_A Loading After (%) | 67.9
TR_B Loading After (%) | 38.2
Minimum Voltage (V) | 212.5