## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 32 | 31 | 31 | 0 | 131 | 3.18 | 50 | 79.6 | 35.3 | 75.8 | 47.6 | 213.6 | 211.8 | 211.8 | YES
2 | OK | 32 | 27 | 27 | 0 | 25.5 | 2.53 | 50 | 79.6 | 35.3 | 76.5 | 37.2 | 214.6 | 214 | 214 | YES
3 | OK | 31 | 98 | 98 | 0 | 169.8 | 2.43 | 50 | 79.6 | 35.3 | 76.7 | 44.7 | 213.8 | 212.4 | 212.4 | YES
4 | OK | 27 | 28 | 28 | 0 | 47.1 | 1.81 | 50 | 79.6 | 35.3 | 77.4 | 42.2 | 214.4 | 212.9 | 212.9 | YES
5 | OK | 3 | 7 | 8 | 10 | 3 | 2.4 | 50 | 79.6 | 35.3 | 76.6 | 44.4 | 215.5 | 212.6 | 212.6 | YES
6 | OK | 3 | 4 | 18 | 3 | 21.9 | 6.91 | 50 | 79.6 | 35.3 | 71.1 | 44.4 | 217.6 | 211.7 | 211.7 | YES
7 | OK | 3 | 6 | 6 | 1 | 110.4 | 6.24 | 50 | 79.6 | 35.3 | 71.9 | 42.8 | 217.3 | 212.8 | 212.8 | YES
8 | OK | 28 | 29 | 29 | 0 | 78.8 | 0.51 | 50 | 79.6 | 35.3 | 79 | 37.2 | 214.5 | 214 | 214 | YES
9 | OK | 7 | 8 | 8 | 10 | 3 | 1.86 | 50 | 79.6 | 35.3 | 77.3 | 42.4 | 215.6 | 213 | 213 | YES
10 | OK | 4 | 5 | 18 | 3 | 21.9 | 5.19 | 50 | 79.6 | 35.3 | 73.2 | 44.4 | 216.4 | 211.7 | 211.7 | YES
11 | OK | 6 | 1 | 0 | 1 | 166.7 | 5.11 | 50 | 79.6 | 35.3 | 73.3 | 42.7 | 216.7 | 212.8 | 212.8 | YES
12 | OK | 8 | 9 | 9 | 10 | 33 | 1.12 | 50 | 79.6 | 35.3 | 78.2 | 39.6 | 215.6 | 213.6 | 213.6 | YES
13 | OK | 5 | 15 | 18 | 3 | 21.9 | 4.35 | 50 | 79.6 | 35.3 | 74.2 | 44.4 | 215.2 | 211.7 | 211.7 | YES
14 | OK | 1 | 0 | 0 | 1 | 166.7 | 4.49 | 50 | 79.6 | 35.3 | 74 | 40.4 | 216.9 | 213.4 | 213.4 | YES
15 | OK | 1 | 122 | 122 | 1 | 173.2 | 0.62 | 50 | 79.6 | 35.3 | 78.9 | 37.7 | 214.3 | 213.9 | 213.9 | YES
16 | OK | 9 | 10 | 10 | 10 | 36.2 | 0.57 | 50 | 79.6 | 35.3 | 78.9 | 37.1 | 214.9 | 214.1 | 214.1 | YES
17 | OK | 15 | 16 | 18 | 3 | 21.9 | 3.8 | 50 | 79.6 | 35.3 | 74.9 | 44.4 | 214.1 | 211.7 | 211.7 | YES
18 | OK | 0 | 100 | 100 | 2 | 167.6 | 3.46 | 50 | 79.6 | 35.3 | 75.3 | 38.7 | 216 | 213.5 | 213.5 | YES
19 | OK | 122 | 51 | 51 | 0 | 185 | 0.16 | 50 | 79.6 | 35.3 | 79.4 | 35.9 | 214.5 | 214.3 | 214.3 | YES
20 | OK | 10 | 96 | 96 | 10 | 71.9 | 0.49 | 50 | 79.6 | 35.3 | 79 | 37.1 | 214.7 | 214.1 | 214.1 | YES
21 | OK | 16 | 17 | 18 | 3 | 21.9 | 0.5 | 50 | 79.6 | 35.3 | 79 | 37.2 | 214.4 | 213.8 | 213.8 | YES
22 | OK | 16 | 24 | 24 | 3 | 98 | 1.81 | 50 | 79.6 | 35.3 | 77.4 | 42.4 | 213.9 | 212.3 | 212.3 | YES
23 | OK | 16 | 19 | 19 | 4 | 59.1 | 1.47 | 50 | 79.6 | 35.3 | 77.8 | 41.1 | 214.3 | 212.5 | 212.5 | YES
24 | OK | 100 | 99 | 99 | 2 | 168.7 | 3.46 | 50 | 79.6 | 35.3 | 75.3 | 38.7 | 216 | 213.5 | 213.5 | YES
25 | OK | 96 | 11 | 11 | 10 | 83.9 | 0.38 | 50 | 79.6 | 35.3 | 79.1 | 36.7 | 214.8 | 214.1 | 214.1 | YES
26 | OK | 24 | 26 | 46 | 2 | 103.7 | 0.55 | 50 | 79.6 | 35.3 | 78.9 | 37.4 | 214.4 | 213.9 | 213.9 | YES
27 | OK | 19 | 20 | 20 | 5 | 59.3 | 1.02 | 50 | 79.6 | 35.3 | 78.3 | 39.3 | 214.5 | 212.9 | 212.9 | YES
28 | OK | 99 | 62 | 62 | 2 | 176.7 | 2.21 | 50 | 79.6 | 35.3 | 76.9 | 38.7 | 215.4 | 213.5 | 213.5 | YES
29 | OK | 11 | 12 | 12 | 10 | 122.6 | 0.21 | 50 | 79.6 | 35.3 | 79.4 | 36.1 | 214.8 | 214.3 | 214.3 | YES
30 | OK | 26 | 25 | 25 | 3 | 138.3 | 0.48 | 50 | 79.6 | 35.3 | 79 | 37.2 | 214.4 | 213.9 | 213.9 | YES
31 | ** OPTIMAL ** | 26 | 46 | 46 | 2 | 103.7 | 0.07 | 50 | 79.6 | 35.3 | 79.5 | 35.5 | 214.5 | 214.4 | 214.4 | YES
32 | OK | 20 | 21 | 21 | 5 | 65.1 | 0.58 | 50 | 79.6 | 35.3 | 78.9 | 37.6 | 214.7 | 213.6 | 213.6 | YES
33 | OK | 62 | 61 | 61 | 3 | 210.6 | 1.87 | 50 | 79.6 | 35.3 | 77.3 | 37.4 | 215.5 | 213.8 | 213.8 | YES
34 | OK | 21 | 22 | 22 | 5 | 90.9 | 0.28 | 50 | 79.6 | 35.3 | 79.3 | 36.4 | 214.8 | 214 | 214 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 27-008210
TR_B (available) | 49-009410
TR_A Rated kVA | 100
TR_B Rated kVA | 30
TR_A Baseline Loading% | 79.6
TR_B Baseline Loading% | 35.3
Total Scenarios Evaluated | 34
Feasible Scenarios | 34
--- Optimal Solution ---
Switch Parent Node | 26
Switch Child Node | 46
Tie Node (TR_A side) | 46
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 103.7
Load Transferred (kW) | 0.07
TR_A Loading After (%) | 79.5
TR_B Loading After (%) | 35.5
Minimum Voltage (V) | 214.4