## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 37 | 39 | 55 | 2 | 3.2 | 13.41 | 50 | 72 | 24.8 | 26.7 | 81.3 | 225.9 | 188.9 | 188.9 | NO
| NG | 39 | 49 | 55 | 2 | 3.2 | 12.84 | 50 | 72 | 24.8 | 28 | 78.6 | 225.9 | 190.4 | 190.4 | NO
| NG | 49 | 26 | 55 | 2 | 3.2 | 12.84 | 50 | 72 | 24.8 | 28 | 78.6 | 225.9 | 190.4 | 190.4 | NO
| NG | 26 | 7 | 55 | 2 | 3.2 | 12.84 | 50 | 72 | 24.8 | 42 | 78.6 | 221.9 | 190.4 | 190.4 | NO
| NG | 7 | 2 | 55 | 2 | 3.2 | 12.84 | 50 | 72 | 24.8 | 42 | 78.6 | 221.9 | 190.4 | 190.4 | NO
| NG | 2 | 0 | 55 | 2 | 3.2 | 12.24 | 50 | 72 | 24.8 | 43.3 | 75.9 | 221.9 | 192 | 192 | NO
1 | OK | 0 | 1 | 55 | 2 | 3.2 | 2.18 | 50 | 72 | 24.8 | 65.4 | 33.2 | 215.4 | 216.6 | 215.4 | YES
2 | OK | 1 | 42 | 55 | 2 | 3.2 | 1.88 | 50 | 72 | 24.8 | 67.6 | 32 | 215.5 | 216.8 | 215.5 | YES
3 | OK | 42 | 51 | 55 | 2 | 3.2 | 1.75 | 50 | 72 | 24.8 | 67.9 | 31.5 | 215.5 | 216.9 | 215.5 | YES
4 | OK | 51 | 52 | 55 | 2 | 3.2 | 0.83 | 50 | 72 | 24.8 | 70 | 28 | 215.6 | 217.6 | 215.6 | YES
5 | OK | 52 | 64 | 55 | 2 | 3.2 | 0.83 | 50 | 72 | 24.8 | 70 | 28 | 215.6 | 217.6 | 215.6 | YES
6 | OK | 64 | 56 | 55 | 2 | 3.2 | 0.63 | 50 | 72 | 24.8 | 70.5 | 27.2 | 215.6 | 217.7 | 215.6 | YES
7 | ** OPTIMAL ** | 56 | 54 | 55 | 2 | 3.2 | 0.03 | 50 | 72 | 24.8 | 71.9 | 24.9 | 215.7 | 218.2 | 215.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 28-004544
TR_B (available) | 64-005539
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 72
TR_B Baseline Loading% | 24.8
Total Scenarios Evaluated | 13
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 56
Switch Child Node | 54
Tie Node (TR_A side) | 55
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 3.2
Load Transferred (kW) | 0.03
TR_A Loading After (%) | 71.9
TR_B Loading After (%) | 24.9
Minimum Voltage (V) | 215.7