## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | ** OPTIMAL ** | 37 | 38 | 36 | 93 | 2.6 | 8.83 | 50 | 72 | 48.6 | 52.2 | 50.7 | 217.1 | 219 | 217.1 | YES
2 | OK | 38 | 12 | 36 | 93 | 2.6 | 7.1 | 50 | 72 | 48.6 | 56.2 | 50.1 | 216.7 | 219 | 216.7 | YES
3 | OK | 12 | 13 | 36 | 93 | 2.6 | 6.46 | 50 | 72 | 48.6 | 57.7 | 50.1 | 216.7 | 219 | 216.7 | YES
4 | OK | 13 | 48 | 36 | 93 | 2.6 | 5.91 | 50 | 72 | 48.6 | 58.9 | 50 | 216.6 | 219 | 216.6 | YES
5 | OK | 48 | 36 | 36 | 93 | 2.6 | 5.89 | 50 | 72 | 48.6 | 59 | 50 | 216.6 | 219 | 216.6 | YES
6 | OK | 36 | 5 | 32 | 92 | 3.2 | 4.64 | 50 | 72 | 48.6 | 61.9 | 50 | 216.6 | 219 | 216.6 | YES
7 | OK | 5 | 6 | 32 | 92 | 3.2 | 3.57 | 50 | 72 | 48.6 | 64.3 | 50 | 216.6 | 219 | 216.6 | YES
8 | OK | 6 | 10 | 4 | 40 | 4.7 | 2.18 | 50 | 72 | 48.6 | 67.5 | 50 | 215.9 | 218.7 | 215.9 | YES
9 | OK | 6 | 35 | 32 | 92 | 3.2 | 1.39 | 50 | 72 | 48.6 | 68.8 | 49.6 | 216.4 | 219 | 216.4 | YES
10 | OK | 10 | 3 | 4 | 40 | 4.7 | 2 | 50 | 72 | 48.6 | 67.9 | 49.4 | 215.9 | 218.6 | 215.9 | YES
| NG | 35 | 33 | 32 | 92 | 3.2 | 0.99 | 50 | 72 | 48.6 | 12.7 | 49.3 | 5.1 | 218.9 | 5.1 | NO
11 | OK | 3 | 4 | 4 | 40 | 4.7 | 0.27 | 50 | 72 | 48.6 | 71.4 | 48.8 | 215.7 | 218.9 | 215.7 | YES
12 | OK | 3 | 11 | 11 | 66 | 34.2 | 1.73 | 50 | 72 | 48.6 | 68.6 | 49.4 | 215.9 | 219 | 215.9 | YES
13 | OK | 33 | 32 | 32 | 92 | 3.2 | 0.11 | 50 | 72 | 48.6 | 71.7 | 48.6 | 215.7 | 218.9 | 215.7 | YES
14 | OK | 11 | 34 | 34 | 66 | 35.8 | 1.05 | 50 | 72 | 48.6 | 70.1 | 48.6 | 215.7 | 218.9 | 215.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 28-004544
TR_B (available) | 65-006095
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 72
TR_B Baseline Loading% | 48.6
Total Scenarios Evaluated | 15
Feasible Scenarios | 14
--- Optimal Solution ---
Switch Parent Node | 37
Switch Child Node | 38
Tie Node (TR_A side) | 36
Tie Node (TR_B side) | 93
Tie Line Distance (m) | 2.6
Load Transferred (kW) | 8.83
TR_A Loading After (%) | 52.2
TR_B Loading After (%) | 50.7
Minimum Voltage (V) | 217.1