## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 17 | 18 | 18 | 10 | 41.4 | 3.03 | 50 | 82.3 | 67.8 | 70.7 | 79.4 | 215.1 | 216.5 | 215.1 | YES
2 | ** OPTIMAL ** | 19 | 20 | 36 | 49 | 64.8 | 2.12 | 50 | 82.3 | 67.8 | 74.1 | 75.9 | 216.1 | 218.2 | 216.1 | YES
3 | OK | 18 | 33 | 33 | 10 | 50.9 | 2.25 | 50 | 82.3 | 67.8 | 73.7 | 74.6 | 215.1 | 217.1 | 215.1 | YES
4 | OK | 20 | 21 | 21 | 49 | 76.5 | 1.72 | 50 | 82.3 | 67.8 | 75.6 | 74.4 | 215.8 | 218.2 | 215.8 | YES
5 | OK | 33 | 31 | 31 | 10 | 66.1 | 1.41 | 50 | 82.3 | 67.8 | 76.9 | 73.2 | 214.4 | 217.1 | 214.4 | YES
6 | OK | 21 | 29 | 29 | 49 | 112.3 | 1.49 | 50 | 82.3 | 67.8 | 76.5 | 73.5 | 215.6 | 218.2 | 215.6 | YES
7 | OK | 8 | 9 | 9 | 49 | 131.7 | 1.1 | 50 | 82.3 | 67.8 | 78 | 72 | 215.9 | 218.2 | 215.9 | YES
8 | OK | 31 | 32 | 32 | 10 | 68.1 | 1.41 | 50 | 82.3 | 67.8 | 76.9 | 67.8 | 214.4 | 218.2 | 214.4 | YES
9 | OK | 9 | 10 | 10 | 49 | 131.8 | 1.1 | 50 | 82.3 | 67.8 | 78 | 67.8 | 215.9 | 218.2 | 215.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 28-007151
TR_B (available) | 52-007783
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.3
TR_B Baseline Loading% | 67.8
Total Scenarios Evaluated | 9
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 19
Switch Child Node | 20
Tie Node (TR_A side) | 36
Tie Node (TR_B side) | 49
Tie Line Distance (m) | 64.8
Load Transferred (kW) | 2.12
TR_A Loading After (%) | 74.1
TR_B Loading After (%) | 75.9
Minimum Voltage (V) | 216.1