## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 36 | 32 | 22 | 64 | 28.6 | 31.4 | 50 | 83.4 | 40.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 36 | 29 | 4 | 42 | 154.9 | 3.85 | 50 | 83.4 | 40.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 32 | 33 | 22 | 64 | 28.6 | 29.73 | 50 | 83.4 | 40.3 | 12.6 | 62.6 | 229.1 | 189.5 | 189.5 | NO
| NG | 29 | 16 | 4 | 42 | 154.9 | 3.85 | 50 | 83.4 | 40.3 | 74.5 | 42.6 | 204.3 | 218.1 | 204.3 | NO
| NG | 33 | 46 | 35 | 42 | 112.2 | 2.34 | 50 | 83.4 | 40.3 | 78 | 42.1 | 203.5 | 217.8 | 203.5 | NO
| NG | 33 | 31 | 22 | 64 | 28.6 | 25.73 | 50 | 83.4 | 40.3 | 21.8 | 60.8 | 228 | 187.9 | 187.9 | NO
| NG | 16 | 53 | 53 | 43 | 167.7 | 1.81 | 50 | 83.4 | 40.3 | 79.2 | 41.6 | 204.1 | 217.9 | 204.1 | NO
| NG | 31 | 30 | 22 | 64 | 28.6 | 24.62 | 50 | 83.4 | 40.3 | 24.3 | 59.9 | 227.3 | 187.1 | 187.1 | NO
| NG | 53 | 25 | 25 | 43 | 169.9 | 1.81 | 50 | 83.4 | 40.3 | 79.2 | 41.6 | 204.1 | 218 | 204.1 | NO
| NG | 30 | 15 | 22 | 64 | 28.6 | 22.33 | 50 | 83.4 | 40.3 | 29.6 | 58.3 | 225.3 | 185.7 | 185.7 | NO
| NG | 30 | 11 | 12 | 42 | 68.4 | 2.29 | 50 | 83.4 | 40.3 | 78 | 42 | 203.3 | 217.8 | 203.3 | NO
| NG | 25 | 24 | 24 | 43 | 192.5 | 1.73 | 50 | 83.4 | 40.3 | 79.4 | 41.6 | 204.1 | 218 | 204.1 | NO
| NG | 15 | 50 | 22 | 64 | 28.6 | 22.33 | 50 | 83.4 | 40.3 | 29.6 | 58.3 | 225.3 | 185.7 | 185.7 | NO
| NG | 50 | 49 | 22 | 64 | 28.6 | 3.17 | 50 | 83.4 | 40.3 | 75.7 | 42.6 | 204.3 | 217.8 | 204.3 | NO
| NG | 50 | 45 | 45 | 43 | 54.7 | 19.16 | 50 | 83.4 | 40.3 | 37.1 | 55.8 | 219.4 | 194 | 194 | NO
| NG | 49 | 51 | 22 | 64 | 28.6 | 3.17 | 50 | 83.4 | 40.3 | 75.7 | 42.6 | 204.3 | 217.8 | 204.3 | NO
1 | OK | 45 | 9 | 9 | 43 | 90.3 | 9.42 | 50 | 83.4 | 40.3 | 60.3 | 47.6 | 214.9 | 213.8 | 213.8 | YES
| NG | 51 | 28 | 22 | 64 | 28.6 | 3.17 | 50 | 83.4 | 40.3 | 75.7 | 42.6 | 204.3 | 217.8 | 204.3 | NO
2 | OK | 9 | 10 | 10 | 43 | 97.8 | 9.42 | 50 | 83.4 | 40.3 | 60.3 | 47.6 | 214.9 | 213.8 | 213.8 | YES
| NG | 28 | 27 | 22 | 64 | 28.6 | 3.15 | 50 | 83.4 | 40.3 | 75.8 | 42.6 | 204.3 | 217.8 | 204.3 | NO
3 | OK | 10 | 44 | 44 | 43 | 132.6 | 9.33 | 50 | 83.4 | 40.3 | 60.5 | 47.5 | 214.9 | 213.8 | 213.8 | YES
| NG | 27 | 23 | 22 | 64 | 28.6 | 2.71 | 50 | 83.4 | 40.3 | 76.8 | 42.2 | 204.4 | 217.8 | 204.4 | NO
4 | OK | 44 | 43 | 43 | 43 | 165.2 | 9.02 | 50 | 83.4 | 40.3 | 61.3 | 47.2 | 214.5 | 214.5 | 214.5 | YES
| NG | 23 | 22 | 22 | 64 | 28.6 | 1.93 | 50 | 83.4 | 40.3 | 78.6 | 41.7 | 204.5 | 217.8 | 204.5 | NO
5 | ** OPTIMAL ** | 43 | 42 | 42 | 43 | 272.8 | 9.01 | 50 | 83.4 | 40.3 | 61.3 | 47.2 | 214.5 | 214.5 | 214.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 28-011934
TR_B (available) | 52-003811
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 83.4
TR_B Baseline Loading% | 40.3
Total Scenarios Evaluated | 25
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 43
Switch Child Node | 42
Tie Node (TR_A side) | 42
Tie Node (TR_B side) | 43
Tie Line Distance (m) | 272.8
Load Transferred (kW) | 9.01
TR_A Loading After (%) | 61.3
TR_B Loading After (%) | 47.2
Minimum Voltage (V) | 214.5