## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 35 | 26 | 21 | 19 | 85.4 | 12.77 | 50 | 86.4 | 5.5 | 9.1 | 65.8 | 226.9 | 172.1 | 172.1 | NO
| NG | 26 | 25 | 21 | 19 | 85.4 | 12.29 | 50 | 86.4 | 5.5 | 11.9 | 62.6 | 226.2 | 175.9 | 175.9 | NO
| NG | 25 | 13 | 21 | 19 | 85.4 | 11.83 | 50 | 86.4 | 5.5 | 14.5 | 59.8 | 225.6 | 179.3 | 179.3 | NO
| NG | 13 | 12 | 21 | 19 | 85.4 | 11.83 | 50 | 86.4 | 5.5 | 14.5 | 59.8 | 225.6 | 179.3 | 179.3 | NO
| NG | 12 | 11 | 21 | 19 | 85.4 | 11.4 | 50 | 86.4 | 5.5 | 17 | 57.2 | 225.1 | 182.3 | 182.3 | NO
| NG | 11 | 10 | 21 | 19 | 85.4 | 10.56 | 50 | 86.4 | 5.5 | 21.8 | 52.4 | 223.9 | 187.4 | 187.4 | NO
| NG | 10 | 9 | 21 | 19 | 85.4 | 9.65 | 50 | 86.4 | 5.5 | 27.1 | 44.8 | 222.7 | 195.2 | 195.2 | NO
| NG | 9 | 4 | 21 | 19 | 85.4 | 9.14 | 50 | 86.4 | 5.5 | 30 | 44.8 | 222 | 195.2 | 195.2 | NO
| NG | 4 | 2 | 21 | 19 | 85.4 | 8.76 | 50 | 86.4 | 5.5 | 32.2 | 42.9 | 221.5 | 197.2 | 197.2 | NO
| NG | 2 | 3 | 21 | 19 | 85.4 | 6.98 | 50 | 86.4 | 5.5 | 42.7 | 34.4 | 217 | 206.3 | 206.3 | NO
| NG | 2 | 8 | 38 | 17 | 113.1 | 1.78 | 50 | 86.4 | 5.5 | 75.1 | 12.5 | 199 | 223.6 | 199 | NO
| NG | 3 | 14 | 21 | 19 | 85.4 | 6.26 | 50 | 86.4 | 5.5 | 47 | 31.2 | 215.4 | 209.5 | 209.5 | NO
| NG | 8 | 7 | 38 | 17 | 113.1 | 1.56 | 50 | 86.4 | 5.5 | 76.5 | 11.6 | 198.4 | 224.4 | 198.4 | NO
1 | OK | 14 | 15 | 21 | 19 | 85.4 | 5.76 | 50 | 86.4 | 5.5 | 49.9 | 28.9 | 214.2 | 211.6 | 211.6 | YES
2 | ** OPTIMAL ** | 15 | 16 | 21 | 19 | 85.4 | 4.99 | 50 | 86.4 | 5.5 | 54.6 | 25.6 | 212.2 | 214.5 | 212.2 | YES
| NG | 16 | 27 | 21 | 19 | 85.4 | 4.22 | 50 | 86.4 | 5.5 | 59.3 | 22.4 | 209.9 | 217.2 | 209.9 | NO
| NG | 27 | 17 | 21 | 19 | 85.4 | 4.22 | 50 | 86.4 | 5.5 | 59.3 | 22.4 | 209.9 | 217.2 | 209.9 | NO
| NG | 17 | 18 | 21 | 19 | 85.4 | 4.11 | 50 | 86.4 | 5.5 | 59.9 | 21.9 | 209.5 | 217.6 | 209.5 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 28-016693
TR_B (available) | 59-006988
TR_A Rated kVA | 20
TR_B Rated kVA | 30
TR_A Baseline Loading% | 86.4
TR_B Baseline Loading% | 5.5
Total Scenarios Evaluated | 18
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 16
Tie Node (TR_A side) | 21
Tie Node (TR_B side) | 19
Tie Line Distance (m) | 85.4
Load Transferred (kW) | 4.99
TR_A Loading After (%) | 54.6
TR_B Loading After (%) | 25.6
Minimum Voltage (V) | 212.2