## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 18 | 17 | 17 | 17 | 238.3 | 20.01 | 50 | 69.6 | 25.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 18 | 19 | 25 | 17 | 178.6 | 9.93 | 50 | 69.6 | 25.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 17 | 16 | 16 | 17 | 259.6 | 18.35 | 50 | 69.6 | 25.6 | 26.7 | 45.9 | 224.9 | 193.7 | 193.7 | NO
1 | OK | 19 | 20 | 25 | 17 | 178.6 | 9 | 50 | 69.6 | 25.6 | 48.8 | 35.1 | 217.9 | 210.8 | 210.8 | YES
2 | OK | 20 | 21 | 25 | 17 | 178.6 | 7.63 | 50 | 69.6 | 25.6 | 51.9 | 31.6 | 217.2 | 214.7 | 214.7 | YES
3 | OK | 21 | 22 | 30 | 17 | 192.7 | 5.47 | 50 | 69.6 | 25.6 | 56.9 | 31.7 | 217.2 | 213 | 213 | YES
4 | OK | 21 | 23 | 25 | 17 | 178.6 | 2.16 | 50 | 69.6 | 25.6 | 64.7 | 25.6 | 216 | 223 | 216 | YES
5 | OK | 22 | 33 | 30 | 17 | 192.7 | 5.15 | 50 | 69.6 | 25.6 | 57.6 | 31.7 | 217.2 | 213 | 213 | YES
6 | OK | 33 | 36 | 30 | 17 | 192.7 | 3.26 | 50 | 69.6 | 25.6 | 62 | 26.9 | 216.3 | 221.1 | 216.3 | YES
7 | OK | 36 | 37 | 30 | 17 | 192.7 | 3.26 | 50 | 69.6 | 25.6 | 62 | 26.9 | 216.3 | 221.1 | 216.3 | YES
8 | ** OPTIMAL ** | 37 | 38 | 30 | 17 | 192.7 | 1 | 50 | 69.6 | 25.6 | 67.3 | 26.9 | 216.3 | 221.1 | 216.3 | YES
9 | OK | 38 | 1 | 30 | 17 | 192.7 | 0.47 | 50 | 69.6 | 25.6 | 68.5 | 25.7 | 216 | 223 | 216 | YES
10 | OK | 1 | 0 | 30 | 17 | 192.7 | 0.47 | 50 | 69.6 | 25.6 | 68.5 | 25.7 | 216 | 223 | 216 | YES
11 | OK | 0 | 28 | 30 | 17 | 192.7 | 0.47 | 50 | 69.6 | 25.6 | 68.5 | 25.7 | 216 | 223 | 216 | YES
12 | OK | 28 | 31 | 30 | 17 | 192.7 | 0.02 | 50 | 69.6 | 25.6 | 69.6 | 25.7 | 216 | 223 | 216 | YES
13 | OK | 31 | 32 | 30 | 17 | 192.7 | 0.02 | 50 | 69.6 | 25.6 | 69.6 | 25.7 | 216 | 223 | 216 | YES
14 | OK | 32 | 29 | 30 | 17 | 192.7 | 0.02 | 50 | 69.6 | 25.6 | 69.6 | 25.7 | 216 | 223 | 216 | YES
15 | OK | 29 | 30 | 30 | 17 | 192.7 | 0.02 | 50 | 69.6 | 25.6 | 69.6 | 25.7 | 216 | 223 | 216 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 29-003030
TR_B (available) | 36-009499
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 69.6
TR_B Baseline Loading% | 25.6
Total Scenarios Evaluated | 18
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 37
Switch Child Node | 38
Tie Node (TR_A side) | 30
Tie Node (TR_B side) | 17
Tie Line Distance (m) | 192.7
Load Transferred (kW) | 1
TR_A Loading After (%) | 67.3
TR_B Loading After (%) | 26.9
Minimum Voltage (V) | 216.3