## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 18 | 19 | 40 | 43 | 3 | 9.93 | 50 | 69.6 | 37.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 19 | 20 | 40 | 43 | 3 | 9 | 50 | 69.6 | 37.5 | 48.8 | 48.1 | 217.9 | 197.6 | 197.6 | NO
| NG | 20 | 21 | 40 | 43 | 3 | 7.63 | 50 | 69.6 | 37.5 | 51.9 | 44.1 | 217.2 | 203.4 | 203.4 | NO
| NG | 21 | 22 | 40 | 43 | 3 | 5.47 | 50 | 69.6 | 37.5 | 56.9 | 44.1 | 217.2 | 203.4 | 203.4 | NO
| NG | 22 | 33 | 40 | 43 | 3 | 5.15 | 50 | 69.6 | 37.5 | 57.6 | 44.1 | 217.2 | 203.4 | 203.4 | NO
| NG | 33 | 36 | 40 | 43 | 3 | 3.26 | 50 | 69.6 | 37.5 | 62 | 39 | 216.3 | 209.5 | 209.5 | NO
| NG | 36 | 37 | 40 | 43 | 3 | 3.26 | 50 | 69.6 | 37.5 | 62 | 39 | 216.3 | 209.5 | 209.5 | NO
| NG | 37 | 38 | 40 | 43 | 3 | 1 | 50 | 69.6 | 37.5 | 67.3 | 39 | 216.3 | 209.5 | 209.5 | NO
1 | ** OPTIMAL ** | 38 | 1 | 1 | 43 | 86.1 | 0.47 | 50 | 69.6 | 37.5 | 68.5 | 37.6 | 216 | 211.1 | 211.1 | YES
| NG | 38 | 39 | 40 | 43 | 3 | 0.53 | 50 | 69.6 | 37.5 | 68.4 | 38.9 | 216.3 | 209.5 | 209.5 | NO
2 | OK | 1 | 0 | 0 | 43 | 87.5 | 0.47 | 50 | 69.6 | 37.5 | 68.5 | 37.6 | 216 | 211.1 | 211.1 | YES
| NG | 39 | 41 | 40 | 43 | 3 | 0.53 | 50 | 69.6 | 37.5 | 68.4 | 38.9 | 216.3 | 209.5 | 209.5 | NO
3 | OK | 0 | 28 | 28 | 43 | 111.5 | 0.47 | 50 | 69.6 | 37.5 | 68.5 | 37.6 | 216 | 211.1 | 211.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 29-003030
TR_B (available) | 56-014222
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 69.6
TR_B Baseline Loading% | 37.5
Total Scenarios Evaluated | 13
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 38
Switch Child Node | 1
Tie Node (TR_A side) | 1
Tie Node (TR_B side) | 43
Tie Line Distance (m) | 86.1
Load Transferred (kW) | 0.47
TR_A Loading After (%) | 68.5
TR_B Loading After (%) | 37.6
Minimum Voltage (V) | 211.1