## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 18 | 17 | 17 | 1 | 104.2 | 20.01 | 50 | 69.6 | 22.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 18 | 19 | 26 | 1 | 40.8 | 9.93 | 50 | 69.6 | 22.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 17 | 16 | 16 | 0 | 113.1 | 18.35 | 50 | 69.6 | 22.1 | 26.7 | 41.1 | 224.9 | 201.5 | 201.5 | NO
1 | OK | 19 | 20 | 26 | 1 | 40.8 | 9 | 50 | 69.6 | 22.1 | 48.8 | 31.1 | 217.9 | 217.5 | 217.5 | YES
| NG | 16 | 15 | 11 | 22 | 123 | 13.31 | 50 | 69.6 | 22.1 | 38.3 | 40.7 | 224.9 | 206.3 | 206.3 | NO
2 | OK | 20 | 21 | 26 | 1 | 40.8 | 7.63 | 50 | 69.6 | 22.1 | 51.9 | 27.8 | 217.2 | 221 | 217.2 | YES
| NG | 15 | 14 | 11 | 22 | 123 | 12.72 | 50 | 69.6 | 22.1 | 39.7 | 39.8 | 224.7 | 207.5 | 207.5 | NO
3 | OK | 21 | 22 | 26 | 1 | 40.8 | 5.47 | 50 | 69.6 | 22.1 | 56.9 | 27.8 | 217.2 | 221 | 217.2 | YES
| NG | 14 | 13 | 11 | 22 | 123 | 11.07 | 50 | 69.6 | 22.1 | 43.5 | 39.1 | 223.9 | 208.3 | 208.3 | NO
4 | OK | 22 | 33 | 26 | 1 | 40.8 | 5.15 | 50 | 69.6 | 22.1 | 57.6 | 27.8 | 217.2 | 221 | 217.2 | YES
| NG | 13 | 12 | 11 | 22 | 123 | 9.98 | 50 | 69.6 | 22.1 | 46.1 | 38 | 223.4 | 209.5 | 209.5 | NO
5 | OK | 33 | 34 | 26 | 1 | 40.8 | 1.89 | 50 | 69.6 | 22.1 | 65.2 | 26.5 | 217 | 222.5 | 217 | YES
6 | OK | 12 | 35 | 11 | 22 | 123 | 8.48 | 50 | 69.6 | 22.1 | 49.5 | 34.1 | 223.7 | 213.7 | 213.7 | YES
7 | OK | 34 | 26 | 26 | 1 | 40.8 | 1.63 | 50 | 69.6 | 22.1 | 65.8 | 25.9 | 216.8 | 222.9 | 216.8 | YES
8 | OK | 35 | 8 | 11 | 22 | 123 | 6.83 | 50 | 69.6 | 22.1 | 53.4 | 32.8 | 222.5 | 215 | 215 | YES
9 | OK | 26 | 27 | 27 | 1 | 43.6 | 1.23 | 50 | 69.6 | 22.1 | 66.7 | 24.9 | 216.6 | 223.2 | 216.6 | YES
10 | ** OPTIMAL ** | 8 | 6 | 11 | 22 | 123 | 4.04 | 50 | 69.6 | 22.1 | 60 | 26.7 | 219.7 | 220.8 | 219.7 | YES
11 | OK | 27 | 2 | 2 | 1 | 64.2 | 0.31 | 50 | 69.6 | 22.1 | 68.9 | 22.8 | 216.1 | 223.7 | 216.1 | YES
12 | OK | 6 | 7 | 11 | 22 | 123 | 0.98 | 50 | 69.6 | 22.1 | 66.7 | 22.3 | 216.6 | 223.8 | 216.6 | YES
13 | OK | 7 | 9 | 11 | 22 | 123 | 0.98 | 50 | 69.6 | 22.1 | 67.3 | 22.3 | 216.1 | 223.8 | 216.1 | YES
14 | OK | 9 | 10 | 11 | 22 | 123 | 0.24 | 50 | 69.6 | 22.1 | 69 | 22.3 | 216.1 | 223.8 | 216.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 29-003030
TR_B (available) | 67-012503
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 69.6
TR_B Baseline Loading% | 22.1
Total Scenarios Evaluated | 21
Feasible Scenarios | 14
--- Optimal Solution ---
Switch Parent Node | 8
Switch Child Node | 6
Tie Node (TR_A side) | 11
Tie Node (TR_B side) | 22
Tie Line Distance (m) | 123
Load Transferred (kW) | 4.04
TR_A Loading After (%) | 60
TR_B Loading After (%) | 26.7
Minimum Voltage (V) | 219.7