## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 53 | 54 | 45 | 7 | 86.3 | 12.72 | 50 | 83.6 | 14.8 | 68.7 | 44.3 | 213.4 | 209.9 | 209.9 | NO
| NG | 54 | 65 | 45 | 7 | 86.3 | 12.72 | 50 | 83.6 | 14.8 | 68.7 | 44.3 | 213.4 | 209.9 | 209.9 | NO
| NG | 65 | 64 | 45 | 7 | 86.3 | 12.12 | 50 | 83.6 | 14.8 | 69.4 | 44.3 | 213.4 | 209.9 | 209.9 | NO
1 | OK | 64 | 63 | 45 | 7 | 86.3 | 10.58 | 50 | 83.6 | 14.8 | 71.2 | 39.2 | 213.5 | 212.9 | 212.9 | YES
2 | ** OPTIMAL ** | 6 | 12 | 47 | 10 | 73.5 | 4.28 | 50 | 83.6 | 14.8 | 78.5 | 31.3 | 214.5 | 222.3 | 214.5 | YES
3 | OK | 6 | 13 | 89 | 8 | 140.2 | 7.33 | 50 | 83.6 | 14.8 | 75 | 38.2 | 214 | 214.9 | 214 | YES
4 | OK | 63 | 61 | 45 | 7 | 86.3 | 4.49 | 50 | 83.6 | 14.8 | 78.3 | 28.3 | 213.4 | 219.3 | 213.4 | YES
5 | OK | 13 | 51 | 89 | 8 | 140.2 | 5.17 | 50 | 83.6 | 14.8 | 77.5 | 32.1 | 213.8 | 218.1 | 213.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 29-005548
TR_B (available) | 60-020504
TR_A Rated kVA | 100
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.6
TR_B Baseline Loading% | 14.8
Total Scenarios Evaluated | 8
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 6
Switch Child Node | 12
Tie Node (TR_A side) | 47
Tie Node (TR_B side) | 10
Tie Line Distance (m) | 73.5
Load Transferred (kW) | 4.28
TR_A Loading After (%) | 78.5
TR_B Loading After (%) | 31.3
Minimum Voltage (V) | 214.5