## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 50 | 51 | 36 | 3 | 164.5 | 17.34 | 50 | 71.9 | 39.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 50 | 52 | 17 | 3 | 238.6 | 13.79 | 50 | 71.9 | 39.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 51 | 68 | 36 | 3 | 164.5 | 17.34 | 50 | 71.9 | 39.5 | 31.8 | 52.1 | 224.6 | 198.2 | 198.2 | NO
| NG | 52 | 69 | 17 | 3 | 238.6 | 13.56 | 50 | 71.9 | 39.5 | 40.6 | 46.2 | 221.1 | 199.7 | 199.7 | NO
| NG | 68 | 43 | 36 | 3 | 164.5 | 15.35 | 50 | 71.9 | 39.5 | 36.3 | 51.8 | 223.8 | 199.7 | 199.7 | NO
| NG | 69 | 56 | 17 | 3 | 238.6 | 13.26 | 50 | 71.9 | 39.5 | 41.3 | 3.6 | 220.9 | 6 | 6 | NO
| NG | 43 | 44 | 36 | 3 | 164.5 | 15.34 | 50 | 71.9 | 39.5 | 36.4 | 51.8 | 223.8 | 199.8 | 199.8 | NO
| NG | 56 | 55 | 17 | 3 | 238.6 | 12.04 | 50 | 71.9 | 39.5 | 44.1 | 45.8 | 220.6 | 199.5 | 199.5 | NO
| NG | 44 | 42 | 36 | 3 | 164.5 | 10.96 | 50 | 71.9 | 39.5 | 46.3 | 48.1 | 222.9 | 207 | 207 | NO
1 | ** OPTIMAL ** | 44 | 65 | 9 | 3 | 172.5 | 3.04 | 50 | 71.9 | 39.5 | 64.9 | 40.9 | 219.7 | 219.8 | 219.7 | YES
| NG | 55 | 59 | 17 | 3 | 238.6 | 11.67 | 50 | 71.9 | 39.5 | 44.9 | 45.4 | 220.6 | 201.4 | 201.4 | NO
| NG | 42 | 0 | 36 | 3 | 164.5 | 10.82 | 50 | 71.9 | 39.5 | 46.7 | 48 | 222.8 | 207 | 207 | NO
2 | OK | 65 | 13 | 9 | 3 | 172.5 | 2.55 | 50 | 71.9 | 39.5 | 66 | 40.6 | 219.4 | 219.6 | 219.4 | YES
| NG | 59 | 26 | 17 | 3 | 238.6 | 9.23 | 50 | 71.9 | 39.5 | 50.6 | 45.1 | 219.6 | 203.3 | 203.3 | NO
| NG | 0 | 1 | 36 | 3 | 164.5 | 8.04 | 50 | 71.9 | 39.5 | 53.1 | 45.8 | 222.3 | 207.7 | 207.7 | NO
3 | OK | 13 | 12 | 9 | 3 | 172.5 | 2.02 | 50 | 71.9 | 39.5 | 67.2 | 40.2 | 219.1 | 219.5 | 219.1 | YES
| NG | 26 | 25 | 17 | 3 | 238.6 | 6.19 | 50 | 71.9 | 39.5 | 57.6 | 43.8 | 218.9 | 205.9 | 205.9 | NO
| NG | 1 | 39 | 36 | 3 | 164.5 | 5.9 | 50 | 71.9 | 39.5 | 58 | 44.2 | 222.3 | 207.6 | 207.6 | NO
4 | OK | 12 | 11 | 9 | 3 | 172.5 | 0.93 | 50 | 71.9 | 39.5 | 69.7 | 40.2 | 219.1 | 219.5 | 219.1 | YES
| NG | 25 | 24 | 17 | 3 | 238.6 | 5.81 | 50 | 71.9 | 39.5 | 58.4 | 43.6 | 218.8 | 205.9 | 205.9 | NO
| NG | 39 | 2 | 36 | 3 | 164.5 | 5.74 | 50 | 71.9 | 39.5 | 58.4 | 44.1 | 222.3 | 208.1 | 208.1 | NO
5 | OK | 11 | 32 | 9 | 3 | 172.5 | 0.67 | 50 | 71.9 | 39.5 | 70.3 | 40 | 218.9 | 219.4 | 218.9 | YES
| NG | 24 | 20 | 17 | 3 | 238.6 | 5.18 | 50 | 71.9 | 39.5 | 59.9 | 43 | 218.8 | 208.8 | 208.8 | NO
6 | OK | 2 | 3 | 3 | 3 | 200.2 | 0.35 | 50 | 71.9 | 39.5 | 71.1 | 39.8 | 218.9 | 219.3 | 218.9 | YES
| NG | 2 | 4 | 36 | 3 | 164.5 | 5.39 | 50 | 71.9 | 39.5 | 59.2 | 43.8 | 222.3 | 209.2 | 209.2 | NO
7 | OK | 32 | 9 | 9 | 3 | 172.5 | 0.67 | 50 | 71.9 | 39.5 | 70.3 | 40 | 218.9 | 219.4 | 218.9 | YES
| NG | 20 | 19 | 17 | 3 | 238.6 | 4.21 | 50 | 71.9 | 39.5 | 62.1 | 42.6 | 218.6 | 208.7 | 208.7 | NO
8 | OK | 3 | 37 | 37 | 3 | 230.8 | 0.13 | 50 | 71.9 | 39.5 | 71.6 | 39.6 | 218.6 | 219.2 | 218.6 | YES
| NG | 4 | 36 | 36 | 3 | 164.5 | 5.35 | 50 | 71.9 | 39.5 | 59.2 | 43.7 | 222.3 | 209.5 | 209.5 | NO
| NG | 19 | 33 | 17 | 3 | 238.6 | 3.85 | 50 | 71.9 | 39.5 | 63 | 42.6 | 218.4 | 208.7 | 208.7 | NO
| NG | 33 | 5 | 17 | 3 | 238.6 | 3.85 | 50 | 71.9 | 39.5 | 63 | 42.6 | 218.4 | 208.7 | 208.7 | NO
| NG | 5 | 6 | 17 | 3 | 238.6 | 3.51 | 50 | 71.9 | 39.5 | 63.7 | 42.3 | 218.4 | 208.6 | 208.6 | NO
9 | OK | 6 | 14 | 17 | 3 | 238.6 | 2.48 | 50 | 71.9 | 39.5 | 66.1 | 41.5 | 218.4 | 212.8 | 212.8 | YES
10 | OK | 14 | 7 | 17 | 3 | 238.6 | 1.85 | 50 | 71.9 | 39.5 | 67.6 | 41 | 218.4 | 215.2 | 215.2 | YES
11 | OK | 7 | 8 | 17 | 3 | 238.6 | 1.07 | 50 | 71.9 | 39.5 | 69.4 | 40.4 | 218.4 | 215.6 | 215.6 | YES
12 | OK | 8 | 17 | 17 | 3 | 238.6 | 0.79 | 50 | 71.9 | 39.5 | 70 | 39.5 | 218.4 | 219.1 | 218.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 29-007512
TR_B (available) | 60-037546
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 71.9
TR_B Baseline Loading% | 39.5
Total Scenarios Evaluated | 36
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 44
Switch Child Node | 65
Tie Node (TR_A side) | 9
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 172.5
Load Transferred (kW) | 3.04
TR_A Loading After (%) | 64.9
TR_B Loading After (%) | 40.9
Minimum Voltage (V) | 219.7