## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 50 | 52 | 60 | 2 | 51.4 | 13.79 | 50 | 71.9 | 0 | 40.1 | 20.6 | 221.1 | 224.4 | 221.1 | YES
2 | ** OPTIMAL ** | 52 | 69 | 60 | 2 | 51.4 | 13.56 | 50 | 71.9 | 0 | 40.6 | 20.6 | 221.1 | 224.4 | 221.1 | YES
| NG | 69 | 56 | 60 | 2 | 51.4 | 13.26 | 50 | 71.9 | 0 | [5 empty] | NO | TR_B sim: not converged
3 | OK | 56 | 55 | 60 | 2 | 51.4 | 12.04 | 50 | 71.9 | 0 | 44.1 | 16.7 | 220.6 | 225.6 | 220.6 | YES
4 | OK | 55 | 59 | 60 | 2 | 51.4 | 11.67 | 50 | 71.9 | 0 | 44.9 | 16.7 | 220.6 | 225.6 | 220.6 | YES
5 | OK | 59 | 26 | 31 | 2 | 59.5 | 9.23 | 50 | 71.9 | 0 | 50.6 | 8.7 | 219.6 | 228.1 | 219.6 | YES
6 | OK | 59 | 61 | 60 | 2 | 51.4 | 2.44 | 50 | 71.9 | 0 | 66.3 | 8 | 219.5 | 228.5 | 219.5 | YES
7 | OK | 26 | 28 | 31 | 2 | 59.5 | 3.04 | 50 | 71.9 | 0 | 64.9 | 5.3 | 219.1 | 229.3 | 219.1 | YES
8 | OK | 61 | 63 | 60 | 2 | 51.4 | 2.44 | 50 | 71.9 | 0 | 66.3 | 7.5 | 219.5 | 228.6 | 219.5 | YES
9 | OK | 28 | 27 | 27 | 2 | 129.4 | 2.49 | 50 | 71.9 | 0 | 66.2 | 5.3 | 219.1 | 229.4 | 219.1 | YES
10 | OK | 28 | 29 | 31 | 2 | 59.5 | 0.55 | 50 | 71.9 | 0 | 70.6 | 0 | 218.4 | 230.9 | 218.4 | YES
11 | OK | 63 | 62 | 60 | 2 | 51.4 | 0.94 | 50 | 71.9 | 0 | 69.7 | 2.2 | 218.7 | 230.4 | 218.7 | YES
12 | OK | 63 | 70 | 70 | 3 | 138 | 1.39 | 50 | 71.9 | 0 | 68.7 | 5.3 | 219.1 | 229.2 | 219.1 | YES
13 | OK | 27 | 64 | 64 | 2 | 136.2 | 1.44 | 50 | 71.9 | 0 | 68.6 | 1.3 | 218.6 | 230.5 | 218.6 | YES
14 | OK | 29 | 30 | 31 | 2 | 59.5 | 0.21 | 50 | 71.9 | 0 | 71.4 | 0 | 218.4 | 230.9 | 218.4 | YES
15 | OK | 62 | 77 | 60 | 2 | 51.4 | 0.86 | 50 | 71.9 | 0 | 69.9 | 2.2 | 218.7 | 230.4 | 218.7 | YES
16 | OK | 77 | 58 | 60 | 2 | 51.4 | 0.86 | 50 | 71.9 | 0 | 69.9 | 2.2 | 218.7 | 230.4 | 218.7 | YES
17 | OK | 58 | 57 | 60 | 2 | 51.4 | 0.86 | 50 | 71.9 | 0 | 69.9 | 2.2 | 218.7 | 230.4 | 218.7 | YES
18 | OK | 57 | 60 | 60 | 2 | 51.4 | 0.35 | 50 | 71.9 | 0 | 71.1 | 0 | 218.6 | 230.9 | 218.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 29-007512
TR_B (available) | 68-010246
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 71.9
TR_B Baseline Loading% | 0
Total Scenarios Evaluated | 19
Feasible Scenarios | 18
--- Optimal Solution ---
Switch Parent Node | 52
Switch Child Node | 69
Tie Node (TR_A side) | 60
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 51.4
Load Transferred (kW) | 13.56
TR_A Loading After (%) | 40.6
TR_B Loading After (%) | 20.6
Minimum Voltage (V) | 221.1