## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 9 | 2 | 52 | 92 | 2.1 | 20.04 | 50 | 82.6 | 47.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 9 | 10 | 45 | 92 | 83.3 | 15.85 | 50 | 82.6 | 47.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 2 | 1 | 52 | 92 | 2.1 | 10.28 | 50 | 82.6 | 47.7 | 56.2 | 53.5 | 222.4 | 200 | 200 | NO
| NG | 10 | 11 | 45 | 92 | 83.3 | 15.85 | 50 | 82.6 | 47.7 | 46.1 | 54.1 | 225.4 | 194.6 | 194.6 | NO
| NG | 1 | 0 | 52 | 92 | 2.1 | 9.34 | 50 | 82.6 | 47.7 | 61.1 | 52.2 | 222.4 | 207.2 | 207.2 | NO
| NG | 11 | 12 | 45 | 92 | 83.3 | 14.31 | 50 | 82.6 | 47.7 | 49.7 | 54.1 | 225 | 194.6 | 194.6 | NO
1 | OK | 0 | 22 | 52 | 92 | 2.1 | 8.39 | 50 | 82.6 | 47.7 | 63.2 | 51.4 | 222.4 | 211 | 211 | YES
2 | OK | 12 | 14 | 45 | 92 | 83.3 | 5.69 | 50 | 82.6 | 47.7 | 67.9 | 51.1 | 223.6 | 210.5 | 210.5 | YES
3 | OK | 22 | 21 | 52 | 92 | 2.1 | 1.54 | 50 | 82.6 | 47.7 | 79.1 | 47.7 | 221.2 | 217.7 | 217.7 | YES
4 | OK | 14 | 27 | 45 | 92 | 83.3 | 5.69 | 50 | 82.6 | 47.7 | 69.5 | 51.1 | 223.3 | 210.5 | 210.5 | YES
5 | OK | 27 | 28 | 45 | 92 | 83.3 | 4.64 | 50 | 82.6 | 47.7 | 71.9 | 50.7 | 222.9 | 212.2 | 212.2 | YES
6 | ** OPTIMAL ** | 28 | 29 | 45 | 92 | 83.3 | 3.19 | 50 | 82.6 | 47.7 | 75.2 | 49.1 | 222.8 | 218.4 | 218.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 29-009894
TR_B (available) | 55-006168
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 82.6
TR_B Baseline Loading% | 47.7
Total Scenarios Evaluated | 12
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 28
Switch Child Node | 29
Tie Node (TR_A side) | 45
Tie Node (TR_B side) | 92
Tie Line Distance (m) | 83.3
Load Transferred (kW) | 3.19
TR_A Loading After (%) | 75.2
TR_B Loading After (%) | 49.1
Minimum Voltage (V) | 218.4