## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 9 | 2 | 20 | 17 | 3.8 | 20.04 | 50 | 82.6 | 41.9 | 36.5 | 51.8 | 224.8 | 198.4 | 198.4 | NO
1 | OK | 2 | 3 | 5 | 13 | 100.7 | 2.9 | 50 | 82.6 | 41.9 | 75.9 | 42.6 | 222.1 | 217.1 | 217.1 | YES
2 | OK | 2 | 1 | 20 | 17 | 3.8 | 10.28 | 50 | 82.6 | 41.9 | 56.2 | 45 | 222.4 | 215.2 | 215.2 | YES
3 | ** OPTIMAL ** | 3 | 4 | 5 | 13 | 100.7 | 2.42 | 50 | 82.6 | 41.9 | 77 | 42.6 | 222.1 | 217.1 | 217.1 | YES
4 | OK | 1 | 0 | 20 | 17 | 3.8 | 9.34 | 50 | 82.6 | 41.9 | 61.1 | 45 | 222.4 | 215.2 | 215.2 | YES
5 | OK | 0 | 22 | 20 | 17 | 3.8 | 8.39 | 50 | 82.6 | 41.9 | 63.2 | 45 | 222.4 | 215.2 | 215.2 | YES
6 | OK | 22 | 21 | 20 | 17 | 3.8 | 1.54 | 50 | 82.6 | 41.9 | 79.1 | 41.9 | 221.2 | 216.9 | 216.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 29-009894
TR_B (available) | 62-001465
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 82.6
TR_B Baseline Loading% | 41.9
Total Scenarios Evaluated | 7
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 4
Tie Node (TR_A side) | 5
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 100.7
Load Transferred (kW) | 2.42
TR_A Loading After (%) | 77
TR_B Loading After (%) | 42.6
Minimum Voltage (V) | 217.1