## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 28 | 27 | 0 | 21 | 191 | 13.41 | 50 | 119 | 15.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 27 | 53 | 0 | 21 | 191 | 12.93 | 50 | 119 | 15.9 | 29.2 | 21.5 | 223.1 | 210.1 | 210.1 | YES
2 | OK | 53 | 43 | 0 | 21 | 191 | 12.35 | 50 | 119 | 15.9 | 32.5 | 21.5 | 223.1 | 210.1 | 210.1 | YES
3 | OK | 43 | 42 | 0 | 21 | 191 | 12.05 | 50 | 119 | 15.9 | 34.3 | 20.7 | 222.7 | 212 | 212 | YES
4 | OK | 42 | 41 | 0 | 21 | 191 | 11.61 | 50 | 119 | 15.9 | 36.8 | 20.7 | 222.7 | 212 | 212 | YES
5 | OK | 41 | 46 | 0 | 21 | 191 | 11.61 | 50 | 119 | 15.9 | 36.8 | 20.7 | 222.7 | 212 | 212 | YES
6 | OK | 46 | 33 | 0 | 21 | 191 | 11.08 | 50 | 119 | 15.9 | 39.9 | 19.3 | 222 | 215.1 | 215.1 | YES
7 | ** OPTIMAL ** | 33 | 32 | 0 | 21 | 191 | 11.03 | 50 | 119 | 15.9 | 40.2 | 19.2 | 221.9 | 215.3 | 215.3 | YES
8 | OK | 32 | 31 | 0 | 21 | 191 | 11.03 | 50 | 119 | 15.9 | 40.2 | 19.2 | 221.9 | 215.3 | 215.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 29-014511
TR_B (available) | 50-003768
TR_A Rated kVA | 20
TR_B Rated kVA | 50
TR_A Baseline Loading% | 119
TR_B Baseline Loading% | 15.9
Total Scenarios Evaluated | 9
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 33
Switch Child Node | 32
Tie Node (TR_A side) | 0
Tie Node (TR_B side) | 21
Tie Line Distance (m) | 191
Load Transferred (kW) | 11.03
TR_A Loading After (%) | 40.2
TR_B Loading After (%) | 19.2
Minimum Voltage (V) | 215.3