## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 76 | 74 | 150 | 33 | 142.7 | 25.4 | 50 | 81.8 | 25.8 | [5 empty] | NO | TR_B sim: not converged
| NG | 22 | 30 | 93 | 33 | 27.8 | 17.34 | 50 | 81.8 | 25.8 | 68.5 | 40.1 | 205.1 | 210 | 205.1 | NO
| NG | 74 | 75 | 150 | 33 | 142.7 | 25.04 | 50 | 81.8 | 25.8 | [5 empty] | NO | TR_B sim: not converged
| NG | 30 | 29 | 93 | 33 | 27.8 | 17.34 | 50 | 81.8 | 25.8 | 68.8 | 40.1 | 205.1 | 210 | 205.1 | NO
| NG | 75 | 124 | 150 | 33 | 142.7 | 21.5 | 50 | 81.8 | 25.8 | [5 empty] | NO | TR_B sim: not converged
| NG | 29 | 28 | 93 | 33 | 27.8 | 14.87 | 50 | 81.8 | 25.8 | 70.6 | 38.4 | 205 | 212.5 | 205 | NO
| NG | 124 | 90 | 150 | 33 | 142.7 | 20.81 | 50 | 81.8 | 25.8 | [5 empty] | NO | TR_B sim: not converged
| NG | 28 | 27 | 93 | 33 | 27.8 | 12.1 | 50 | 81.8 | 25.8 | 72.7 | 36.3 | 204.9 | 215.4 | 204.9 | NO
| NG | 90 | 89 | 150 | 33 | 142.7 | 19.27 | 50 | 81.8 | 25.8 | [5 empty] | NO | TR_B sim: not converged
| NG | 27 | 91 | 93 | 33 | 27.8 | 10.45 | 50 | 81.8 | 25.8 | 73.9 | 34.2 | 204.8 | 217.9 | 204.8 | NO
| NG | 89 | 88 | 150 | 33 | 142.7 | 17.27 | 50 | 81.8 | 25.8 | 68.2 | 88.1 | 215.8 | 135.9 | 135.9 | NO
| NG | 91 | 85 | 93 | 33 | 27.8 | 5.99 | 50 | 81.8 | 25.8 | 77.2 | 26.8 | 204.3 | 225 | 204.3 | NO
| NG | 88 | 7 | 150 | 33 | 142.7 | 16.1 | 50 | 81.8 | 25.8 | 69.1 | 79.2 | 215.8 | 149.5 | 149.5 | NO
| NG | 85 | 70 | 70 | 33 | 64.1 | 3.7 | 50 | 81.8 | 25.8 | 78.9 | 34.8 | 204.3 | 217 | 204.3 | NO
| NG | 7 | 5 | 150 | 33 | 142.7 | 13.23 | 50 | 81.8 | 25.8 | 71.3 | 65 | 215.6 | 170.7 | 170.7 | NO
| NG | 70 | 71 | 71 | 33 | 94.2 | 3.7 | 50 | 81.8 | 25.8 | 78.9 | 34.8 | 204.3 | 217.2 | 204.3 | NO
| NG | 5 | 6 | 150 | 33 | 142.7 | 12.04 | 50 | 81.8 | 25.8 | 72.2 | 60.3 | 215.6 | 177.4 | 177.4 | NO
1 | ** OPTIMAL ** | 6 | 3 | 3 | 33 | 184.6 | 9.64 | 50 | 81.8 | 25.8 | 73.6 | 37.4 | 214.8 | 211.8 | 211.8 | YES
| NG | 3 | 4 | 168 | 33 | 188.9 | 6.95 | 50 | 81.8 | 25.8 | 76.2 | 43.9 | 211 | 200.7 | 200.7 | NO
| NG | 4 | 166 | 168 | 33 | 188.9 | 6.95 | 50 | 81.8 | 25.8 | [5 empty] | NO | TR_B sim: loading 0.7% despite baseline 25.8% (degenerate)

## Summary
Parameter | Value
TR_A (overloaded) | 30-001335
TR_B (available) | 00-051318
TR_A Rated kVA | 160
TR_B Rated kVA | 50
TR_A Baseline Loading% | 81.8
TR_B Baseline Loading% | 25.8
Total Scenarios Evaluated | 20
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 6
Switch Child Node | 3
Tie Node (TR_A side) | 3
Tie Node (TR_B side) | 33
Tie Line Distance (m) | 184.6
Load Transferred (kW) | 9.64
TR_A Loading After (%) | 73.6
TR_B Loading After (%) | 37.4
Minimum Voltage (V) | 211.8