## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 11 | 10 | 15 | 5 | 1.9 | 15.07 | 50 | 97.6 | 29.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 10 | 9 | 15 | 5 | 1.9 | 14.48 | 50 | 97.6 | 29.2 | 41.2 | 86.3 | 219.6 | 213 | 213 | NO
1 | OK | 9 | 8 | 15 | 5 | 1.9 | 11.7 | 50 | 97.6 | 29.2 | 51.8 | 75.1 | 217.5 | 212.2 | 212.2 | YES
2 | OK | 8 | 7 | 15 | 5 | 1.9 | 10.44 | 50 | 97.6 | 29.2 | 51.8 | 69.8 | 217.5 | 216 | 216 | YES
3 | OK | 7 | 6 | 15 | 5 | 1.9 | 10.44 | 50 | 97.6 | 29.2 | 56.7 | 69.8 | 217.5 | 216 | 216 | YES
4 | OK | 6 | 5 | 15 | 5 | 1.9 | 8.28 | 50 | 97.6 | 29.2 | 65 | 61.2 | 217.6 | 220.5 | 217.6 | YES
5 | ** OPTIMAL ** | 5 | 4 | 15 | 5 | 1.9 | 6.95 | 50 | 97.6 | 29.2 | 70.2 | 56 | 217.6 | 220.4 | 217.6 | YES
6 | OK | 4 | 16 | 15 | 5 | 1.9 | 6.64 | 50 | 97.6 | 29.2 | 71.3 | 54.8 | 217.4 | 220.8 | 217.4 | YES
7 | OK | 16 | 26 | 15 | 5 | 1.9 | 5.49 | 50 | 97.6 | 29.2 | 75.8 | 50.3 | 216.5 | 223.2 | 216.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 30-003729
TR_B (available) | 47-000519
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 97.6
TR_B Baseline Loading% | 29.2
Total Scenarios Evaluated | 9
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 4
Tie Node (TR_A side) | 15
Tie Node (TR_B side) | 5
Tie Line Distance (m) | 1.9
Load Transferred (kW) | 6.95
TR_A Loading After (%) | 70.2
TR_B Loading After (%) | 56
Minimum Voltage (V) | 217.6