## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 24 | 25 | 25 | 79 | 87.5 | 1.57 | 50 | 80.9 | 39.4 | 77.3 | 40.6 | 214.2 | 216.8 | 214.2 | YES
| NG | 24 | 26 | 26 | 79 | 96.9 | 12.63 | 50 | 80.9 | 39.4 | 51.7 | 49.1 | 216.9 | 209.4 | 209.4 | NO
| NG | 24 | 31 | 32 | 77 | 52.4 | 20.52 | 50 | 80.9 | 39.4 | 32.6 | 56.2 | 223.9 | 190.8 | 190.8 | NO
| NG | 26 | 28 | 28 | 79 | 100.7 | 12.63 | 50 | 80.9 | 39.4 | 51.8 | 49.1 | 216.8 | 209.4 | 209.4 | NO
| NG | 31 | 41 | 41 | 79 | 69.2 | 20.52 | 50 | 80.9 | 39.4 | 32.6 | 55.9 | 223.9 | 196.4 | 196.4 | NO
2 | OK | 28 | 27 | 27 | 79 | 106.8 | 10.37 | 50 | 80.9 | 39.4 | 57.1 | 47.3 | 215.7 | 214.1 | 214.1 | YES
3 | OK | 27 | 39 | 39 | 79 | 108.8 | 9.89 | 50 | 80.9 | 39.4 | 58.2 | 46.9 | 215.7 | 214.2 | 214.2 | YES
4 | ** OPTIMAL ** | 39 | 19 | 19 | 79 | 116.1 | 9.09 | 50 | 80.9 | 39.4 | 60 | 46.3 | 215.6 | 215.3 | 215.3 | YES
5 | OK | 19 | 17 | 17 | 79 | 127.2 | 9.09 | 50 | 80.9 | 39.4 | 60 | 46.3 | 215.6 | 215.2 | 215.2 | YES
6 | OK | 17 | 18 | 18 | 79 | 134.8 | 7.81 | 50 | 80.9 | 39.4 | 62.9 | 45.3 | 215.2 | 216.1 | 215.2 | YES
7 | OK | 18 | 42 | 42 | 79 | 136.8 | 7.5 | 50 | 80.9 | 39.4 | 63.6 | 45.1 | 215 | 215.9 | 215 | YES
| NG | 42 | 14 | 14 | 79 | 138.7 | 7.5 | 50 | 80.9 | 39.4 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 39.4% (degenerate)

## Summary
Parameter | Value
TR_A (overloaded) | 30-006927
TR_B (available) | 30-006045
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 80.9
TR_B Baseline Loading% | 39.4
Total Scenarios Evaluated | 12
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 39
Switch Child Node | 19
Tie Node (TR_A side) | 19
Tie Node (TR_B side) | 79
Tie Line Distance (m) | 116.1
Load Transferred (kW) | 9.09
TR_A Loading After (%) | 60
TR_B Loading After (%) | 46.3
Minimum Voltage (V) | 215.3