## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 24 | 25 | 30 | 85 | 169 | 1.57 | 95 | 80.9 | 2.8 | 77.3 | 3.4 | 214.2 | 228.1 | 214.2 | YES
2 | ** OPTIMAL ** | 24 | 26 | 57 | 45 | 77 | 12.63 | 50 | 80.9 | 2.8 | 51.7 | 4.7 | 216.9 | 220.6 | 216.9 | YES
3 | OK | 26 | 28 | 57 | 45 | 77 | 12.63 | 50 | 80.9 | 2.8 | 51.8 | 4.7 | 216.8 | 220.6 | 216.8 | YES
4 | OK | 28 | 27 | 6 | 65 | 108.8 | 10.37 | 95 | 80.9 | 2.8 | 57.1 | 6.7 | 215.7 | 224.1 | 215.7 | YES
5 | OK | 28 | 57 | 57 | 45 | 77 | 2.26 | 50 | 80.9 | 2.8 | 75.6 | 3.6 | 215.4 | 226.2 | 215.4 | YES
6 | OK | 27 | 39 | 6 | 65 | 108.8 | 9.89 | 95 | 80.9 | 2.8 | 58.2 | 6.5 | 215.7 | 223.8 | 215.7 | YES
7 | OK | 57 | 61 | 61 | 45 | 120.5 | 2.26 | 50 | 80.9 | 2.8 | 75.6 | 3.6 | 215.4 | 226.7 | 215.4 | YES
8 | OK | 39 | 19 | 6 | 65 | 108.8 | 9.09 | 95 | 80.9 | 2.8 | 60 | 6.2 | 215.6 | 224.3 | 215.6 | YES
9 | OK | 61 | 58 | 59 | 17 | 133.9 | 1.32 | 50 | 80.9 | 2.8 | 77.8 | 3.3 | 214.9 | 225.2 | 214.9 | YES
10 | OK | 19 | 17 | 6 | 65 | 108.8 | 9.09 | 95 | 80.9 | 2.8 | 60 | 6.2 | 215.6 | 224.3 | 215.6 | YES
11 | OK | 58 | 60 | 60 | 45 | 182.6 | 1.32 | 50 | 80.9 | 2.8 | 77.8 | 3.3 | 214.9 | 227.6 | 214.9 | YES
12 | OK | 17 | 18 | 6 | 65 | 108.8 | 7.81 | 95 | 80.9 | 2.8 | 62.9 | 5.7 | 215.2 | 225.8 | 215.2 | YES
13 | OK | 18 | 42 | 6 | 65 | 108.8 | 7.5 | 95 | 80.9 | 2.8 | 63.6 | 5.6 | 215 | 225.8 | 215 | YES
| NG | 42 | 14 | 6 | 65 | 108.8 | 7.5 | 95 | 80.9 | 2.8 | 63.6 | 0 | 215 | 10 | 10 | NO
14 | OK | 14 | 49 | 6 | 65 | 108.8 | 6.1 | 95 | 80.9 | 2.8 | 66.8 | 5 | 214.8 | 227.2 | 214.8 | YES
15 | OK | 49 | 12 | 6 | 65 | 108.8 | 5.99 | 95 | 80.9 | 2.8 | 67.1 | 5 | 214.8 | 227.3 | 214.8 | YES
16 | OK | 12 | 13 | 13 | 85 | 144.9 | 1.41 | 95 | 80.9 | 2.8 | 77.6 | 3.3 | 214.3 | 227.7 | 214.3 | YES
17 | OK | 12 | 50 | 6 | 65 | 108.8 | 4.58 | 95 | 80.9 | 2.8 | 70 | 4.5 | 214.8 | 227.4 | 214.8 | YES
18 | OK | 50 | 43 | 6 | 65 | 108.8 | 4.4 | 95 | 80.9 | 2.8 | 70.8 | 4.4 | 214.6 | 227.4 | 214.6 | YES
19 | OK | 43 | 44 | 44 | 85 | 125.8 | 1.33 | 95 | 80.9 | 2.8 | 77.8 | 3.3 | 214.2 | 228 | 214.2 | YES
20 | OK | 43 | 8 | 6 | 65 | 108.8 | 3.07 | 95 | 80.9 | 2.8 | 73.8 | 3.9 | 214.6 | 227.2 | 214.6 | YES
21 | OK | 44 | 22 | 22 | 85 | 128.8 | 1.33 | 95 | 80.9 | 2.8 | 77.8 | 3.3 | 214.2 | 228 | 214.2 | YES
22 | OK | 8 | 9 | 6 | 65 | 108.8 | 0.98 | 95 | 80.9 | 2.8 | 78.6 | 3.1 | 214.3 | 227.6 | 214.3 | YES
23 | OK | 8 | 37 | 37 | 34 | 120.8 | 0.58 | 50 | 80.9 | 2.8 | 79.5 | 3 | 214.5 | 227.6 | 214.5 | YES
24 | OK | 9 | 7 | 6 | 65 | 108.8 | 0.79 | 95 | 80.9 | 2.8 | 79.1 | 3.1 | 214.3 | 227.6 | 214.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 30-006927
TR_B (available) | 66-012434
TR_A Rated kVA | 50
TR_B Rated kVA | 315
TR_A Baseline Loading% | 80.9
TR_B Baseline Loading% | 2.8
Total Scenarios Evaluated | 25
Feasible Scenarios | 24
--- Optimal Solution ---
Switch Parent Node | 24
Switch Child Node | 26
Tie Node (TR_A side) | 57
Tie Node (TR_B side) | 45
Tie Line Distance (m) | 77
Load Transferred (kW) | 12.63
TR_A Loading After (%) | 51.7
TR_B Loading After (%) | 4.7
Minimum Voltage (V) | 216.9