## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 15 | 1 | 32 | 2 | 38.7 | 12.73 | 50 | 77.9 | 5.8 | 3.1 | 57.8 | 230.2 | 201.8 | 201.8 | NO
| NG | 1 | 2 | 32 | 2 | 38.7 | 11.51 | 50 | 77.9 | 5.8 | 10.1 | 52.4 | 228.2 | 204.4 | 204.4 | NO
| NG | 2 | 3 | 32 | 2 | 38.7 | 9.89 | 50 | 77.9 | 5.8 | 19.4 | 45.5 | 226 | 207.8 | 207.8 | NO
| NG | 3 | 34 | 32 | 2 | 38.7 | 9.05 | 50 | 77.9 | 5.8 | 24.2 | 42 | 224.9 | 209.4 | 209.4 | NO
1 | ** OPTIMAL ** | 34 | 4 | 32 | 2 | 38.7 | 8.48 | 50 | 77.9 | 5.8 | 27.5 | 39.7 | 224 | 210.6 | 210.6 | YES
| NG | 4 | 6 | 32 | 2 | 38.7 | 2.91 | 50 | 77.9 | 5.8 | 60.4 | 17 | 208.4 | 225.5 | 208.4 | NO
| NG | 6 | 7 | 32 | 2 | 38.7 | 2.51 | 50 | 77.9 | 5.8 | 62.8 | 15.5 | 207.5 | 226.2 | 207.5 | NO
| NG | 7 | 38 | 32 | 2 | 38.7 | 1.9 | 50 | 77.9 | 5.8 | 66.4 | 11 | 206.3 | 227.9 | 206.3 | NO
| NG | 38 | 11 | 32 | 2 | 38.7 | 0.87 | 50 | 77.9 | 5.8 | 72.6 | 9.2 | 204 | 228.6 | 204 | NO
| NG | 11 | 12 | 32 | 2 | 38.7 | 0.66 | 50 | 77.9 | 5.8 | 73.9 | 8.4 | 203.6 | 228.9 | 203.6 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 32-001660
TR_B (available) | 60-029540
TR_A Rated kVA | 20
TR_B Rated kVA | 30
TR_A Baseline Loading% | 77.9
TR_B Baseline Loading% | 5.8
Total Scenarios Evaluated | 10
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 34
Switch Child Node | 4
Tie Node (TR_A side) | 32
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 38.7
Load Transferred (kW) | 8.48
TR_A Loading After (%) | 27.5
TR_B Loading After (%) | 39.7
Minimum Voltage (V) | 210.6