## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 15 | 1 | 29 | 23 | 68.1 | 12.73 | 50 | 77.9 | 30.6 | 3.1 | 88 | 230.2 | 182.1 | 182.1 | NO
| NG | 1 | 2 | 29 | 23 | 68.1 | 11.51 | 50 | 77.9 | 30.6 | 10.1 | 81.5 | 228.2 | 186.6 | 186.6 | NO
| NG | 1 | 20 | 25 | 26 | 120.5 | 1.22 | 50 | 77.9 | 30.6 | 70.8 | 35.5 | 204.1 | 217.4 | 204.1 | NO
| NG | 2 | 3 | 29 | 23 | 68.1 | 9.89 | 50 | 77.9 | 30.6 | 19.4 | 73.4 | 226 | 192 | 192 | NO
| NG | 20 | 33 | 25 | 26 | 120.5 | 1.22 | 50 | 77.9 | 30.6 | 70.8 | 35.5 | 204.1 | 217.4 | 204.1 | NO
| NG | 3 | 34 | 29 | 23 | 68.1 | 9.05 | 50 | 77.9 | 30.6 | 24.2 | 69.4 | 224.9 | 194.7 | 194.7 | NO
| NG | 33 | 24 | 25 | 26 | 120.5 | 1.03 | 50 | 77.9 | 30.6 | 71.9 | 34.7 | 203.8 | 217.8 | 203.8 | NO
| NG | 34 | 4 | 29 | 23 | 68.1 | 8.48 | 50 | 77.9 | 30.6 | 27.5 | 66.7 | 224 | 196.4 | 196.4 | NO
| NG | 24 | 25 | 25 | 26 | 120.5 | 0.33 | 50 | 77.9 | 30.6 | 76 | 31.9 | 202.6 | 219.6 | 202.6 | NO
| NG | 4 | 5 | 29 | 23 | 68.1 | 5.57 | 50 | 77.9 | 30.6 | 44.4 | 53.7 | 217.7 | 204.8 | 204.8 | NO
| NG | 5 | 23 | 29 | 23 | 68.1 | 5.08 | 50 | 77.9 | 30.6 | 47.2 | 51.6 | 216.8 | 206.1 | 206.1 | NO
| NG | 23 | 16 | 16 | 23 | 132.1 | 3.99 | 50 | 77.9 | 30.6 | 53.6 | 46.9 | 214.6 | 209.3 | 209.3 | NO
| NG | 23 | 28 | 29 | 23 | 68.1 | 1.09 | 50 | 77.9 | 30.6 | 71.2 | 34.9 | 204.8 | 218.9 | 204.8 | NO
1 | ** OPTIMAL ** | 16 | 17 | 17 | 23 | 135.8 | 3.94 | 50 | 77.9 | 30.6 | 53.9 | 46.7 | 214.5 | 210 | 210 | YES
| NG | 28 | 21 | 29 | 23 | 68.1 | 1.09 | 50 | 77.9 | 30.6 | 71.2 | 34.9 | 204.8 | 218.9 | 204.8 | NO
| NG | 21 | 22 | 29 | 23 | 68.1 | 0.86 | 50 | 77.9 | 30.6 | 72.6 | 34 | 204.2 | 219.2 | 204.2 | NO
| NG | 22 | 29 | 29 | 23 | 68.1 | 0.51 | 50 | 77.9 | 30.6 | 74.8 | 32.6 | 203.4 | 219.6 | 203.4 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 32-001660
TR_B (available) | 66-013678
TR_A Rated kVA | 20
TR_B Rated kVA | 30
TR_A Baseline Loading% | 77.9
TR_B Baseline Loading% | 30.6
Total Scenarios Evaluated | 17
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 17
Tie Node (TR_A side) | 17
Tie Node (TR_B side) | 23
Tie Line Distance (m) | 135.8
Load Transferred (kW) | 3.94
TR_A Loading After (%) | 53.9
TR_B Loading After (%) | 46.7
Minimum Voltage (V) | 210