## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 10 | 11 | 24 | 0 | 14.7 | 12.43 | 50 | 82.7 | 21.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 11 | 34 | 24 | 0 | 14.7 | 11.85 | 50 | 82.7 | 21.7 | 35.8 | 70.1 | 220.6 | 205.2 | 205.2 | NO
| NG | 34 | 12 | 24 | 0 | 14.7 | 11.46 | 50 | 82.7 | 21.7 | 37.3 | 68.4 | 220.5 | 205.9 | 205.9 | NO
| NG | 12 | 13 | 24 | 0 | 14.7 | 10.44 | 50 | 82.7 | 21.7 | 41.2 | 64.2 | 219.8 | 205.5 | 205.5 | NO
| NG | 13 | 14 | 24 | 0 | 14.7 | 9.57 | 50 | 82.7 | 21.7 | 44.5 | 60.5 | 219.6 | 207.2 | 207.2 | NO
| NG | 14 | 32 | 24 | 0 | 14.7 | 9.11 | 50 | 82.7 | 21.7 | 46.3 | 58.5 | 219.6 | 208.6 | 208.6 | NO
1 | OK | 32 | 20 | 24 | 0 | 14.7 | 8.08 | 50 | 82.7 | 21.7 | 50.2 | 54 | 219.6 | 211.5 | 211.5 | YES
2 | OK | 20 | 21 | 24 | 0 | 14.7 | 7.05 | 50 | 82.7 | 21.7 | 54.2 | 50 | 218.9 | 211.1 | 211.1 | YES
3 | OK | 21 | 22 | 24 | 0 | 14.7 | 6.94 | 50 | 82.7 | 21.7 | 54.6 | 49.6 | 218.8 | 211 | 211 | YES
4 | OK | 22 | 23 | 24 | 0 | 14.7 | 5.32 | 50 | 82.7 | 21.7 | 60.9 | 42.8 | 218.7 | 215.2 | 215.2 | YES
5 | OK | 23 | 24 | 24 | 0 | 14.7 | 5.16 | 50 | 82.7 | 21.7 | 61.6 | 42.2 | 218.7 | 215.6 | 215.6 | YES
6 | OK | 24 | 25 | 25 | 0 | 47.6 | 4.94 | 50 | 82.7 | 21.7 | 62.4 | 41.3 | 218.7 | 216.4 | 216.4 | YES
7 | ** OPTIMAL ** | 25 | 26 | 26 | 0 | 93.7 | 4.26 | 50 | 82.7 | 21.7 | 65.1 | 38.5 | 218.2 | 218.4 | 218.2 | YES
8 | OK | 26 | 27 | 27 | 0 | 100.2 | 3.41 | 50 | 82.7 | 21.7 | 68.4 | 35.2 | 218.1 | 217.9 | 217.9 | YES
9 | OK | 27 | 28 | 28 | 0 | 123.9 | 3.22 | 50 | 82.7 | 21.7 | 69.2 | 34.5 | 217.9 | 217.8 | 217.8 | YES
10 | OK | 28 | 29 | 29 | 0 | 132.4 | 2.6 | 50 | 82.7 | 21.7 | 69.2 | 31.9 | 217.9 | 219.8 | 217.9 | YES
11 | OK | 29 | 17 | 17 | 0 | 133.4 | 2.6 | 50 | 82.7 | 21.7 | 69.2 | 31.9 | 217.9 | 220.4 | 217.9 | YES
12 | OK | 17 | 18 | 18 | 0 | 149.5 | 2.6 | 50 | 82.7 | 21.7 | 71.7 | 31.9 | 217.5 | 220.7 | 217.5 | YES
13 | OK | 18 | 30 | 30 | 0 | 197.2 | 2.13 | 50 | 82.7 | 21.7 | 73.6 | 30 | 215.8 | 222.3 | 215.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 33-004768
TR_B (available) | 42-010108
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.7
TR_B Baseline Loading% | 21.7
Total Scenarios Evaluated | 19
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 25
Switch Child Node | 26
Tie Node (TR_A side) | 26
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 93.7
Load Transferred (kW) | 4.26
TR_A Loading After (%) | 65.1
TR_B Loading After (%) | 38.5
Minimum Voltage (V) | 218.2