## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | ** OPTIMAL ** | 10 | 9 | 15 | 29 | 165.2 | 8.65 | 50 | 82.7 | 27.7 | 49 | 38 | 210.4 | 213.9 | 210.4 | YES
2 | OK | 9 | 8 | 15 | 29 | 165.2 | 8.53 | 50 | 82.7 | 27.7 | 49.4 | 37.9 | 210.3 | 213.8 | 210.3 | YES
| NG | 8 | 7 | 15 | 29 | 165.2 | 7.08 | 50 | 82.7 | 27.7 | 55 | 36 | 209.9 | 218.5 | 209.9 | NO
| NG | 7 | 6 | 15 | 29 | 165.2 | 6.53 | 50 | 82.7 | 27.7 | 57.1 | 35.4 | 209.9 | 220.8 | 209.9 | NO
| NG | 6 | 5 | 15 | 29 | 165.2 | 6.1 | 50 | 82.7 | 27.7 | 58.7 | 34.8 | 209.7 | 221.3 | 209.7 | NO
| NG | 5 | 4 | 15 | 29 | 165.2 | 6.01 | 50 | 82.7 | 27.7 | 59.1 | 34.7 | 209.7 | 221.6 | 209.7 | NO
| NG | 4 | 3 | 15 | 29 | 165.2 | 5.44 | 50 | 82.7 | 27.7 | 61.3 | 34 | 209.4 | 222.1 | 209.4 | NO
| NG | 3 | 33 | 15 | 29 | 165.2 | 5 | 50 | 82.7 | 27.7 | 63 | 33.5 | 209.4 | 223.4 | 209.4 | NO
| NG | 33 | 2 | 15 | 29 | 165.2 | 5 | 50 | 82.7 | 27.7 | 63 | 33.5 | 209.4 | 223.4 | 209.4 | NO
| NG | 2 | 1 | 15 | 29 | 165.2 | 4.35 | 50 | 82.7 | 27.7 | 65.5 | 32.7 | 209.4 | 223.8 | 209.4 | NO
| NG | 1 | 0 | 15 | 29 | 165.2 | 2.58 | 50 | 82.7 | 27.7 | 72.4 | 30.7 | 208.2 | 225.9 | 208.2 | NO
| NG | 0 | 19 | 15 | 29 | 165.2 | 1.91 | 50 | 82.7 | 27.7 | 75 | 29.9 | 208 | 226.9 | 208 | NO
| NG | 19 | 16 | 15 | 29 | 165.2 | 1.03 | 50 | 82.7 | 27.7 | 78.6 | 28.9 | 207.3 | 226.8 | 207.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 33-004768
TR_B (available) | 63-004245
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 82.7
TR_B Baseline Loading% | 27.7
Total Scenarios Evaluated | 13
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 9
Tie Node (TR_A side) | 15
Tie Node (TR_B side) | 29
Tie Line Distance (m) | 165.2
Load Transferred (kW) | 8.65
TR_A Loading After (%) | 49
TR_B Loading After (%) | 38
Minimum Voltage (V) | 210.4