## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 7 | 5 | 1 | 4 | 3.4 | 7.67 | 50 | 93.9 | 12.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 5 | 6 | 1 | 4 | 3.4 | 5.81 | 50 | 93.9 | 12.1 | 26.3 | 34.7 | 220.3 | 220.1 | 220.1 | YES
2 | OK | 6 | 0 | 1 | 4 | 3.4 | 5.49 | 50 | 93.9 | 12.1 | 30 | 33.4 | 218.8 | 220.7 | 218.8 | YES
3 | OK | 0 | 1 | 1 | 4 | 3.4 | 4.43 | 50 | 93.9 | 12.1 | 42.2 | 29.2 | 213.8 | 222.4 | 213.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 33-006826
TR_B (available) | 55-015104
TR_A Rated kVA | 10
TR_B Rated kVA | 30
TR_A Baseline Loading% | 93.9
TR_B Baseline Loading% | 12.1
Total Scenarios Evaluated | 4
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 6
Tie Node (TR_A side) | 1
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 3.4
Load Transferred (kW) | 5.81
TR_A Loading After (%) | 26.3
TR_B Loading After (%) | 34.7
Minimum Voltage (V) | 220.1