## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 7 | 32 | 31 | 46 | 2.8 | 0.55 | 50 | 76.5 | 45.2 | 75.2 | 45.2 | 220.9 | 223.9 | 220.9 | YES
2 | OK | 7 | 12 | 23 | 46 | 2.3 | 17.94 | 50 | 76.5 | 45.2 | 33.8 | 54 | 224.2 | 214.8 | 214.8 | YES
3 | OK | 32 | 29 | 31 | 46 | 2.8 | 0.38 | 50 | 76.5 | 45.2 | 75.6 | 45.2 | 220.9 | 223.9 | 220.9 | YES
4 | OK | 12 | 8 | 23 | 46 | 2.3 | 17.51 | 50 | 76.5 | 45.2 | 34.8 | 53.6 | 224.2 | 215.5 | 215.5 | YES
5 | ** OPTIMAL ** | 29 | 31 | 31 | 46 | 2.8 | 0.38 | 50 | 76.5 | 45.2 | 75.6 | 45.2 | 220.9 | 223.9 | 220.9 | YES
6 | OK | 8 | 13 | 23 | 46 | 2.3 | 15.61 | 50 | 76.5 | 45.2 | 39.2 | 53.6 | 223.3 | 215.5 | 215.5 | YES
7 | OK | 13 | 1 | 23 | 46 | 2.3 | 9.67 | 50 | 76.5 | 45.2 | 52.8 | 52.1 | 222.8 | 218.5 | 218.5 | YES
8 | OK | 1 | 0 | 23 | 46 | 2.3 | 5.8 | 50 | 76.5 | 45.2 | 61.7 | 52.1 | 220.8 | 218.5 | 218.5 | YES
9 | OK | 0 | 10 | 23 | 46 | 2.3 | 5.8 | 50 | 76.5 | 45.2 | 61.7 | 52.1 | 220.8 | 218.5 | 218.5 | YES
10 | OK | 10 | 9 | 23 | 46 | 2.3 | 3.98 | 50 | 76.5 | 45.2 | 65.9 | 49.8 | 220.8 | 221.8 | 220.8 | YES
11 | OK | 9 | 27 | 23 | 46 | 2.3 | 3.98 | 50 | 76.5 | 45.2 | 65.9 | 49.8 | 220.8 | 221.8 | 220.8 | YES
12 | OK | 27 | 28 | 23 | 46 | 2.3 | 3.98 | 50 | 76.5 | 45.2 | 65.9 | 49.8 | 220.8 | 221.8 | 220.8 | YES
13 | OK | 28 | 26 | 23 | 46 | 2.3 | 3.98 | 50 | 76.5 | 45.2 | 65.9 | 49.8 | 220.8 | 221.8 | 220.8 | YES
14 | OK | 26 | 25 | 23 | 46 | 2.3 | 3.98 | 50 | 76.5 | 45.2 | 66.3 | 49.8 | 220.8 | 221.8 | 220.8 | YES
15 | OK | 25 | 24 | 23 | 46 | 2.3 | 1.58 | 50 | 76.5 | 45.2 | 71.9 | 47 | 220.8 | 223.6 | 220.8 | YES
16 | OK | 25 | 22 | 22 | 46 | 76.1 | 2.4 | 50 | 76.5 | 45.2 | 70.8 | 48 | 220.8 | 223.4 | 220.8 | YES
17 | OK | 24 | 33 | 23 | 46 | 2.3 | 1.16 | 50 | 76.5 | 45.2 | 72.8 | 45.9 | 220.8 | 223.8 | 220.8 | YES
18 | OK | 22 | 11 | 11 | 46 | 113.1 | 1.03 | 50 | 76.5 | 45.2 | 74 | 46.4 | 220.9 | 223.7 | 220.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 34-004214
TR_B (available) | 57-002592
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 76.5
TR_B Baseline Loading% | 45.2
Total Scenarios Evaluated | 18
Feasible Scenarios | 18
--- Optimal Solution ---
Switch Parent Node | 29
Switch Child Node | 31
Tie Node (TR_A side) | 31
Tie Node (TR_B side) | 46
Tie Line Distance (m) | 2.8
Load Transferred (kW) | 0.38
TR_A Loading After (%) | 75.6
TR_B Loading After (%) | 45.2
Minimum Voltage (V) | 220.9