## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 7 | 32 | 31 | 14 | 6.4 | 0.55 | 50 | 76.5 | 37.4 | 75.2 | 37.4 | 220.9 | 224.8 | 220.9 | YES
| NG | 7 | 12 | 23 | 14 | 3.1 | 17.94 | 50 | 76.5 | 37.4 | 33.8 | 56.2 | 224.2 | 202.2 | 202.2 | NO
2 | OK | 32 | 29 | 31 | 14 | 6.4 | 0.38 | 50 | 76.5 | 37.4 | 75.6 | 37.4 | 220.9 | 224.8 | 220.9 | YES
| NG | 12 | 8 | 23 | 14 | 3.1 | 17.51 | 50 | 76.5 | 37.4 | 34.8 | 55.4 | 224.2 | 203.3 | 203.3 | NO
3 | ** OPTIMAL ** | 29 | 31 | 31 | 14 | 6.4 | 0.38 | 50 | 76.5 | 37.4 | 75.6 | 37.4 | 220.9 | 224.8 | 220.9 | YES
| NG | 8 | 13 | 23 | 14 | 3.1 | 15.61 | 50 | 76.5 | 37.4 | 39.2 | 55.4 | 223.3 | 203.3 | 203.3 | NO
| NG | 13 | 1 | 23 | 14 | 3.1 | 9.67 | 50 | 76.5 | 37.4 | 52.8 | 51.9 | 222.8 | 208.2 | 208.2 | NO
| NG | 1 | 0 | 23 | 14 | 3.1 | 5.8 | 50 | 76.5 | 37.4 | 61.7 | 51.9 | 220.8 | 208.2 | 208.2 | NO
| NG | 0 | 10 | 23 | 14 | 3.1 | 5.8 | 50 | 76.5 | 37.4 | 61.7 | 51.9 | 220.8 | 208.2 | 208.2 | NO
4 | OK | 10 | 9 | 23 | 14 | 3.1 | 3.98 | 50 | 76.5 | 37.4 | 65.9 | 47.1 | 220.8 | 213.8 | 213.8 | YES
5 | OK | 9 | 27 | 23 | 14 | 3.1 | 3.98 | 50 | 76.5 | 37.4 | 65.9 | 47.1 | 220.8 | 213.8 | 213.8 | YES
6 | OK | 27 | 28 | 23 | 14 | 3.1 | 3.98 | 50 | 76.5 | 37.4 | 65.9 | 47.1 | 220.8 | 213.8 | 213.8 | YES
7 | OK | 28 | 26 | 23 | 14 | 3.1 | 3.98 | 50 | 76.5 | 37.4 | 65.9 | 47.1 | 220.8 | 213.8 | 213.8 | YES
8 | OK | 26 | 25 | 23 | 14 | 3.1 | 3.98 | 50 | 76.5 | 37.4 | 66.3 | 47.1 | 220.8 | 213.8 | 213.8 | YES
9 | OK | 25 | 24 | 23 | 14 | 3.1 | 1.58 | 50 | 76.5 | 37.4 | 71.9 | 41.1 | 220.8 | 220.8 | 220.8 | YES
10 | OK | 25 | 22 | 22 | 14 | 74.8 | 2.4 | 50 | 76.5 | 37.4 | 70.8 | 43.2 | 220.8 | 218.2 | 218.2 | YES
11 | OK | 24 | 33 | 23 | 14 | 3.1 | 1.16 | 50 | 76.5 | 37.4 | 72.8 | 38.9 | 220.8 | 223.2 | 220.8 | YES
12 | OK | 22 | 11 | 11 | 14 | 112.4 | 1.03 | 50 | 76.5 | 37.4 | 74 | 39.8 | 220.9 | 221.9 | 220.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 34-004214
TR_B (available) | 67-012619
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 76.5
TR_B Baseline Loading% | 37.4
Total Scenarios Evaluated | 18
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 29
Switch Child Node | 31
Tie Node (TR_A side) | 31
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 6.4
Load Transferred (kW) | 0.38
TR_A Loading After (%) | 75.6
TR_B Loading After (%) | 37.4
Minimum Voltage (V) | 220.9