## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 7 | 6 | 4 | 62 | 21.2 | 7.34 | 50 | 76.5 | 34 | 0 | 36.1 | 20 | 223.3 | 20 | NO
1 | OK | 7 | 12 | 12 | 62 | 55.7 | 17.94 | 50 | 76.5 | 34 | 33.8 | 39.6 | 224.2 | 212.3 | 212.3 | YES
2 | OK | 6 | 5 | 4 | 62 | 21.2 | 5.05 | 50 | 76.5 | 34 | 63.9 | 34.7 | 221 | 224 | 221 | YES
3 | OK | 12 | 8 | 8 | 62 | 80.3 | 17.51 | 50 | 76.5 | 34 | 34.8 | 39.4 | 224.2 | 212.7 | 212.7 | YES
4 | OK | 5 | 4 | 4 | 62 | 21.2 | 0.18 | 50 | 76.5 | 34 | 76.1 | 34.1 | 220.6 | 224 | 220.6 | YES
5 | OK | 5 | 15 | 15 | 62 | 38.3 | 4.87 | 50 | 76.5 | 34 | 64.3 | 34.5 | 220.9 | 224 | 220.9 | YES
6 | OK | 8 | 13 | 13 | 62 | 86.4 | 15.61 | 50 | 76.5 | 34 | 39.2 | 39.4 | 223.3 | 212.7 | 212.7 | YES
7 | OK | 15 | 21 | 21 | 62 | 58.9 | 4.87 | 50 | 76.5 | 34 | 65.3 | 34.5 | 220.9 | 224 | 220.9 | YES
8 | ** OPTIMAL ** | 13 | 14 | 14 | 62 | 88.5 | 5.94 | 50 | 76.5 | 34 | 62.8 | 34.9 | 221.2 | 224.1 | 221.2 | YES
9 | OK | 13 | 1 | 1 | 62 | 91.5 | 9.67 | 50 | 76.5 | 34 | 52.8 | 38.4 | 222.8 | 214.8 | 214.8 | YES
10 | OK | 21 | 20 | 20 | 62 | 84.3 | 3.51 | 50 | 76.5 | 34 | 68.4 | 34.5 | 220.9 | 224 | 220.9 | YES
11 | OK | 14 | 16 | 16 | 62 | 92.5 | 4.09 | 50 | 76.5 | 34 | 67.1 | 34.4 | 220.8 | 224 | 220.8 | YES
12 | OK | 1 | 0 | 0 | 62 | 120.4 | 5.8 | 50 | 76.5 | 34 | 61.7 | 38.4 | 220.8 | 214.8 | 214.8 | YES
13 | OK | 20 | 19 | 19 | 51 | 88 | 0.94 | 50 | 76.5 | 34 | 74.3 | 34.7 | 220.5 | 224 | 220.5 | YES
14 | OK | 16 | 17 | 17 | 62 | 106 | 2.3 | 50 | 76.5 | 34 | 71.2 | 34.3 | 220.7 | 224 | 220.7 | YES
15 | OK | 0 | 10 | 10 | 62 | 143.6 | 5.8 | 50 | 76.5 | 34 | 61.7 | 38.4 | 220.8 | 214.8 | 214.8 | YES
16 | OK | 17 | 18 | 18 | 62 | 124.6 | 0.73 | 50 | 76.5 | 34 | 74.8 | 34.3 | 220.7 | 224 | 220.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 34-004214
TR_B (available) | 67-028785
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 76.5
TR_B Baseline Loading% | 34
Total Scenarios Evaluated | 17
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 13
Switch Child Node | 14
Tie Node (TR_A side) | 14
Tie Node (TR_B side) | 62
Tie Line Distance (m) | 88.5
Load Transferred (kW) | 5.94
TR_A Loading After (%) | 62.8
TR_B Loading After (%) | 34.9
Minimum Voltage (V) | 221.2