## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 7 | 6 | 0 | 7 | 2.3 | 11.53 | 50 | 47.8 | 37.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 6 | 5 | 0 | 7 | 2.3 | 9.55 | 50 | 47.8 | 37.6 | 36.8 | 48.7 | 222.1 | 221.1 | 221.1 | YES
2 | OK | 5 | 33 | 0 | 7 | 2.3 | 8.59 | 50 | 47.8 | 37.6 | 37.9 | 47.6 | 221.9 | 221 | 221 | YES
3 | OK | 33 | 4 | 0 | 7 | 2.3 | 8.59 | 50 | 47.8 | 37.6 | 37.9 | 47.6 | 221.9 | 221 | 221 | YES
4 | OK | 4 | 3 | 0 | 7 | 2.3 | 5.81 | 50 | 47.8 | 37.6 | 41.1 | 44.3 | 221.9 | 222.2 | 221.9 | YES
5 | ** OPTIMAL ** | 3 | 36 | 0 | 7 | 2.3 | 5.43 | 50 | 47.8 | 37.6 | 41.6 | 43.8 | 221.9 | 222.2 | 221.9 | YES
6 | OK | 36 | 29 | 0 | 7 | 2.3 | 4.4 | 50 | 47.8 | 37.6 | 42.7 | 42.6 | 221.7 | 222.2 | 221.7 | YES
7 | OK | 29 | 19 | 0 | 7 | 2.3 | 4.4 | 50 | 47.8 | 37.6 | 42.7 | 42.6 | 221.7 | 222.2 | 221.7 | YES
8 | OK | 19 | 14 | 0 | 7 | 2.3 | 3.73 | 50 | 47.8 | 37.6 | 43.5 | 41.9 | 221.5 | 222.2 | 221.5 | YES
9 | OK | 14 | 2 | 0 | 7 | 2.3 | 2.63 | 50 | 47.8 | 37.6 | 44.8 | 40.6 | 221.5 | 222.3 | 221.5 | YES
10 | OK | 2 | 1 | 0 | 7 | 2.3 | 1.76 | 50 | 47.8 | 37.6 | 45.8 | 39.6 | 221.3 | 222.4 | 221.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 35-010258
TR_B (available) | 50-005683
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 47.8
TR_B Baseline Loading% | 37.6
Total Scenarios Evaluated | 11
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 36
Tie Node (TR_A side) | 0
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 2.3
Load Transferred (kW) | 5.43
TR_A Loading After (%) | 41.6
TR_B Loading After (%) | 43.8
Minimum Voltage (V) | 221.9