## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 7 | 8 | 15 | 68 | 25.6 | 29.7 | 50 | 47.8 | 50 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 8 | 35 | 15 | 68 | 25.6 | 28.26 | 50 | 47.8 | 50 | 14.9 | 90.1 | 226.5 | 182 | 182 | NO
| NG | 35 | 37 | 15 | 68 | 25.6 | 28.17 | 50 | 47.8 | 50 | 15 | 90 | 226.5 | 182.6 | 182.6 | NO
| NG | 37 | 9 | 15 | 68 | 25.6 | 25.12 | 50 | 47.8 | 50 | 18.5 | 84.9 | 226.1 | 186.3 | 186.3 | NO
| NG | 9 | 10 | 15 | 68 | 25.6 | 23.75 | 50 | 47.8 | 50 | 20.1 | 82.9 | 226.1 | 185.6 | 185.6 | NO
| NG | 10 | 30 | 15 | 68 | 25.6 | 22.24 | 50 | 47.8 | 50 | 21.8 | 80.6 | 226 | 189 | 189 | NO
| NG | 30 | 32 | 15 | 68 | 25.6 | 21.87 | 50 | 47.8 | 50 | 21.8 | 80.1 | 226 | 188.9 | 188.9 | NO
| NG | 32 | 34 | 15 | 68 | 25.6 | 21.87 | 50 | 47.8 | 50 | 22.2 | 79.8 | 226 | 188.6 | 188.6 | NO
| NG | 34 | 11 | 15 | 68 | 25.6 | 20.42 | 50 | 47.8 | 50 | [5 empty] | NO | TR_A sim: loading 2158% (degenerate)
| NG | 11 | 12 | 15 | 68 | 25.6 | 17.72 | 50 | 47.8 | 50 | 27 | 73.9 | 225.7 | 194.1 | 194.1 | NO
| NG | 12 | 13 | 15 | 68 | 25.6 | 13.88 | 50 | 47.8 | 50 | 31.5 | 68.2 | 225.3 | 202.5 | 202.5 | NO
| NG | 13 | 20 | 15 | 68 | 25.6 | 13.88 | 50 | 47.8 | 50 | 31.5 | 68.2 | 225.3 | 202.5 | 202.5 | NO
| NG | 20 | 28 | 15 | 68 | 25.6 | 13.71 | 50 | 47.8 | 50 | 31.6 | 67.9 | 225.3 | 202.5 | 202.5 | NO
| NG | 28 | 18 | 15 | 68 | 25.6 | 11.34 | 50 | 47.8 | 50 | 34.4 | 64.7 | 225.1 | 205.4 | 205.4 | NO
1 | ** OPTIMAL ** | 18 | 16 | 15 | 68 | 25.6 | 4.14 | 50 | 47.8 | 50 | 42.7 | 53.3 | 221.4 | 213.9 | 213.9 | YES
2 | OK | 16 | 17 | 15 | 68 | 25.6 | 0.98 | 50 | 47.8 | 50 | 46.7 | 51.2 | 221.4 | 213.3 | 213.3 | YES
3 | OK | 17 | 15 | 15 | 68 | 25.6 | 0.67 | 50 | 47.8 | 50 | 47 | 50.9 | 221.5 | 213.3 | 213.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 35-010258
TR_B (available) | 59-027328
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 47.8
TR_B Baseline Loading% | 50
Total Scenarios Evaluated | 17
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 18
Switch Child Node | 16
Tie Node (TR_A side) | 15
Tie Node (TR_B side) | 68
Tie Line Distance (m) | 25.6
Load Transferred (kW) | 4.14
TR_A Loading After (%) | 42.7
TR_B Loading After (%) | 53.3
Minimum Voltage (V) | 213.9