## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 31 | 11 | 8 | 6 | 7.8 | 3.46 | 50 | 83.8 | 57.7 | 70.6 | 57.7 | 213.9 | 214.4 | 213.9 | YES
2 | OK | 30 | 29 | 38 | 4 | 136.8 | 1.59 | 50 | 83.8 | 57.7 | 77.7 | 64.1 | 215.2 | 212 | 212 | YES
3 | OK | 11 | 9 | 8 | 6 | 7.8 | 2.04 | 50 | 83.8 | 57.7 | 76 | 57.7 | 213.9 | 214.4 | 213.9 | YES
4 | OK | 29 | 34 | 38 | 4 | 136.8 | 1.32 | 50 | 83.8 | 57.7 | 78.7 | 63 | 215 | 212.5 | 212.5 | YES
5 | ** OPTIMAL ** | 9 | 8 | 8 | 6 | 7.8 | 1.29 | 50 | 83.8 | 57.7 | 78.9 | 57.7 | 213.9 | 214.4 | 213.9 | YES
6 | OK | 34 | 38 | 38 | 4 | 136.8 | 1.32 | 50 | 83.8 | 57.7 | 78.7 | 63 | 215 | 212.5 | 212.5 | YES
| NG | 7 | 4 | 33 | 0 | 100.3 | 5.42 | 50 | 83.8 | 57.7 | 62.7 | 78.6 | 218.2 | 209.9 | 209.9 | NO
7 | OK | 7 | 35 | 1 | 0 | 130 | 2.21 | 50 | 83.8 | 57.7 | 75.2 | 66.2 | 215.7 | 212.6 | 212.6 | YES
8 | OK | 4 | 5 | 33 | 0 | 100.3 | 3.75 | 50 | 83.8 | 57.7 | 69.2 | 72.1 | 216.9 | 211.3 | 211.3 | YES
9 | OK | 4 | 10 | 10 | 13 | 102 | 1.67 | 50 | 83.8 | 57.7 | 77.3 | 64.2 | 215.3 | 212.4 | 212.4 | YES
10 | OK | 35 | 0 | 1 | 0 | 130 | 1.19 | 50 | 83.8 | 57.7 | 79.2 | 62.2 | 214.9 | 213.4 | 213.4 | YES
11 | OK | 5 | 2 | 33 | 0 | 100.3 | 3.6 | 50 | 83.8 | 57.7 | 69.8 | 71.5 | 216.8 | 211.5 | 211.5 | YES
12 | OK | 2 | 3 | 33 | 0 | 100.3 | 2.15 | 50 | 83.8 | 57.7 | 75.4 | 65.9 | 215.6 | 212.6 | 212.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 35-015455
TR_B (available) | 51-002099
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.8
TR_B Baseline Loading% | 57.7
Total Scenarios Evaluated | 13
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 8
Tie Node (TR_A side) | 8
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 7.8
Load Transferred (kW) | 1.29
TR_A Loading After (%) | 78.9
TR_B Loading After (%) | 57.7
Minimum Voltage (V) | 213.9