## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | ** OPTIMAL ** | 35 | 36 | 37 | 39 | 82.7 | 4.92 | 50 | 87.8 | 55 | 39.5 | 59 | 217.3 | 213.8 | 213.8 | YES
| NG | 35 | 46 | 46 | 39 | 162.6 | 8.21 | 50 | 87.8 | 55 | 65.1 | 70.6 | 214.8 | 209.4 | 209.4 | NO
| NG | 46 | 47 | 47 | 39 | 198.9 | 6.87 | 50 | 87.8 | 55 | 68.2 | 70.6 | 214.8 | 209.4 | 209.4 | NO
| NG | 53 | 56 | 56 | 39 | 165.1 | 5.12 | 50 | 87.8 | 55 | 75.6 |  | 213.5 | 5.0808e+58 | 213.5 | NO
2 | OK | 47 | 39 | 18 | 39 | 226.3 | 6.64 | 50 | 87.8 | 55 | 68.7 | 60.5 | 214.7 | 211.4 | 211.4 | YES
| NG | 39 | 40 | 40 | 39 | 241 | 5.66 | 50 | 87.8 | 55 | 73 | 67.5 | 214.7 | 209.5 | 209.5 | NO
3 | OK | 40 | 41 | 41 | 39 | 276 | 5.49 | 50 | 87.8 | 55 | 73.3 | 67.1 | 214.6 | 210.2 | 210.2 | YES
| NG | 9 | 10 | 15 | 39 | 224.2 | 10.93 | 50 | 87.8 | 55 |  | 73.5 | 5.7 | 198.4 | 5.7 | NO
4 | OK | 10 | 11 | 11 | 39 | 238.5 | 4.78 | 50 | 87.8 | 55 | 74.1 | 59.6 | 213.6 | 215.7 | 213.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 35-015823
TR_B (available) | 35-008703
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 87.8
TR_B Baseline Loading% | 55
Total Scenarios Evaluated | 9
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 35
Switch Child Node | 36
Tie Node (TR_A side) | 37
Tie Node (TR_B side) | 39
Tie Line Distance (m) | 82.7
Load Transferred (kW) | 4.92
TR_A Loading After (%) | 39.5
TR_B Loading After (%) | 59
Minimum Voltage (V) | 213.8