## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 54 | 7 | 25 | 11 | 3.9 | 4.68 | 50 | 39.6 | 27.9 | 27.7 | 46.4 | 222.4 | 219.9 | 219.9 | YES
2 | OK | 54 | 52 | 52 | 11 | 7 | 0.18 | 50 | 39.6 | 27.9 | 39.6 | 27.9 | 220.2 | 224.3 | 220.2 | YES
3 | OK | 7 | 6 | 25 | 11 | 3.9 | 4.68 | 50 | 39.6 | 27.9 | 27.7 | 46.4 | 222.5 | 219.9 | 219.9 | YES
4 | OK | 52 | 59 | 59 | 11 | 120.1 | 0.18 | 50 | 39.6 | 27.9 | 39.6 | 27.9 | 220.2 | 224.3 | 220.2 | YES
5 | OK | 8 | 57 | 57 | 11 | 63.1 | 1.66 | 50 | 39.6 | 27.9 | 36.5 | 27.9 | 220.9 | 224.3 | 220.9 | YES
6 | OK | 6 | 25 | 25 | 11 | 3.9 | 4.68 | 50 | 39.6 | 27.9 | 28 | 46.4 | 222.4 | 219.9 | 219.9 | YES
| NG | 9 | 12 | 12 | 11 | 71.2 | 10.19 | 50 | 39.6 | 27.9 | 33.5 | 72.9 | 221.5 | 187.7 | 187.7 | NO
7 | OK | 9 | 11 | 23 | 11 | 65.1 | 8.27 | 50 | 39.6 | 27.9 | 18 | 61.4 | 225.3 | 211.1 | 211.1 | YES
8 | OK | 57 | 55 | 58 | 11 | 67.9 | 0.96 | 50 | 39.6 | 27.9 | 39.2 | 27.9 | 220.3 | 224.3 | 220.3 | YES
9 | OK | 57 | 73 | 73 | 11 | 96.2 | 0.7 | 50 | 39.6 | 27.9 | 36.9 | 27.9 | 220.7 | 224.3 | 220.7 | YES
10 | OK | 25 | 26 | 26 | 11 | 5.9 | 4.68 | 50 | 39.6 | 27.9 | 28 | 46.4 | 222.4 | 219.9 | 219.9 | YES
| NG | 12 | 67 | 67 | 11 | 97.1 | 10.19 | 50 | 39.6 | 27.9 | 33.5 | 72.8 | 221.5 | 187.8 | 187.8 | NO
11 | OK | 11 | 10 | 23 | 11 | 65.1 | 7.11 | 50 | 39.6 | 27.9 | 20.3 | 56.5 | 224.8 | 213 | 213 | YES
12 | OK | 55 | 56 | 56 | 11 | 192 | 0.65 | 50 | 39.6 | 27.9 | 39.3 | 27.9 | 220.3 | 224.3 | 220.3 | YES
13 | OK | 55 | 58 | 58 | 11 | 67.9 | 0.31 | 50 | 39.6 | 27.9 | 39.5 | 27.9 | 220.2 | 224.3 | 220.2 | YES
14 | OK | 73 | 68 | 68 | 11 | 101.6 | 0.7 | 50 | 39.6 | 27.9 | 36.9 | 27.9 | 220.7 | 224.3 | 220.7 | YES
15 | OK | 26 | 24 | 24 | 11 | 19.8 | 4.68 | 50 | 39.6 | 27.9 | 28 | 46.4 | 222.4 | 219.9 | 219.9 | YES
| NG | 67 | 16 | 16 | 11 | 103.1 | 10.19 | 50 | 39.6 | 27.9 | 33.5 | 72.8 | 221.5 | 187.8 | 187.8 | NO
16 | OK | 10 | 29 | 29 | 11 | 87.7 | 7.11 | 50 | 39.6 | 27.9 | 20.5 | 56.5 | 224.8 | 213.4 | 213.4 | YES
17 | ** OPTIMAL ** | 24 | 2 | 2 | 11 | 53.2 | 3.22 | 50 | 39.6 | 27.9 | 31 | 40.6 | 221.8 | 221.9 | 221.8 | YES
18 | OK | 24 | 30 | 30 | 11 | 25.2 | 1.46 | 50 | 39.6 | 27.9 | 36.6 | 33.6 | 220.8 | 222.6 | 220.8 | YES
| NG | 16 | 17 | 17 | 11 | 143.8 | 9.99 | 50 | 39.6 | 27.9 | 36.2 | 71.8 | 220.9 | 188.6 | 188.6 | NO
19 | OK | 29 | 45 | 45 | 11 | 112.3 | 6.88 | 50 | 39.6 | 27.9 | 21.1 | 55.5 | 224.7 | 214.1 | 214.1 | YES
20 | OK | 2 | 3 | 3 | 11 | 85.3 | 2.78 | 50 | 39.6 | 27.9 | 31.4 | 38.8 | 221.8 | 222.2 | 221.8 | YES
21 | OK | 30 | 31 | 31 | 11 | 56.9 | 1.14 | 50 | 39.6 | 27.9 | 37.8 | 32.4 | 220.5 | 222.5 | 220.5 | YES
22 | OK | 17 | 18 | 18 | 11 | 170.8 | 2.07 | 50 | 39.6 | 27.9 | 37.2 | 36.1 | 220.7 | 217.5 | 217.5 | YES
23 | OK | 45 | 22 | 22 | 11 | 114.7 | 6.88 | 50 | 39.6 | 27.9 | 21.1 | 55.2 | 224.7 | 214.4 | 214.4 | YES
24 | OK | 3 | 46 | 46 | 11 | 88.4 | 2.34 | 50 | 39.6 | 27.9 | 33 | 37.1 | 221.4 | 223.2 | 221.4 | YES
25 | OK | 31 | 33 | 33 | 11 | 85.9 | 0.95 | 50 | 39.6 | 27.9 | 38.5 | 31.7 | 220.4 | 222.4 | 220.4 | YES
26 | OK | 18 | 74 | 74 | 11 | 174.4 | 1.87 | 50 | 39.6 | 27.9 | 37.2 | 32.9 | 220.7 | 219.4 | 219.4 | YES
27 | OK | 22 | 15 | 15 | 11 | 127.7 | 5.87 | 50 | 39.6 | 27.9 | 24.9 | 51 | 224 | 215.7 | 215.7 | YES
28 | OK | 46 | 47 | 47 | 11 | 118.6 | 2.12 | 50 | 39.6 | 27.9 | 33.3 | 36.2 | 221.4 | 223.6 | 221.4 | YES
29 | OK | 33 | 32 | 32 | 11 | 113.2 | 0.76 | 50 | 39.6 | 27.9 | 38.5 | 30.9 | 220.4 | 223 | 220.4 | YES
30 | OK | 74 | 65 | 65 | 11 | 215.1 | 1.25 | 50 | 39.6 | 27.9 | 37.9 | 32.9 | 220.5 | 219.4 | 219.4 | YES
31 | OK | 15 | 14 | 14 | 11 | 137.2 | 0.82 | 50 | 39.6 | 27.9 | 37.9 | 31.1 | 220.7 | 223.4 | 220.7 | YES
32 | OK | 15 | 41 | 41 | 11 | 132.5 | 5.05 | 50 | 39.6 | 27.9 | 26.6 | 45.5 | 223.6 | 218.4 | 218.4 | YES
33 | OK | 47 | 4 | 4 | 11 | 122.3 | 2.12 | 50 | 39.6 | 27.9 | 33.3 | 36.2 | 221.4 | 223.6 | 221.4 | YES
34 | OK | 32 | 28 | 28 | 11 | 126.9 | 0.28 | 50 | 39.6 | 27.9 | 38.5 | 29 | 220.4 | 224.4 | 220.4 | YES
35 | OK | 65 | 19 | 19 | 11 | 254.8 | 1.12 | 50 | 39.6 | 27.9 | 38.4 | 32.4 | 220.4 | 219.3 | 219.3 | YES
36 | OK | 41 | 42 | 42 | 11 | 143.4 | 3.97 | 50 | 39.6 | 27.9 | 28.7 | 43.6 | 223.2 | 218.1 | 218.1 | YES
37 | OK | 4 | 5 | 5 | 11 | 151.3 | 1.69 | 50 | 39.6 | 27.9 | 35 | 34.5 | 221.1 | 223.4 | 221.1 | YES
38 | OK | 42 | 0 | 0 | 11 | 191.4 | 1.1 | 50 | 39.6 | 27.9 | 39 | 32.4 | 220.4 | 217.4 | 217.4 | YES
39 | OK | 5 | 48 | 48 | 11 | 184.1 | 1.66 | 50 | 39.6 | 27.9 | 35.1 | 34.4 | 221 | 223.4 | 221 | YES
40 | OK | 48 | 49 | 49 | 11 | 226.4 | 0.46 | 50 | 39.6 | 27.9 | 38.7 | 29.7 | 220.3 | 223.7 | 220.3 | YES
41 | OK | 49 | 75 | 75 | 11 | 266.8 | 0.28 | 50 | 39.6 | 27.9 | 38.7 | 29 | 220.3 | 224.3 | 220.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 36-012323
TR_B (available) | 65-000218
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 39.6
TR_B Baseline Loading% | 27.9
Total Scenarios Evaluated | 45
Feasible Scenarios | 41
--- Optimal Solution ---
Switch Parent Node | 24
Switch Child Node | 2
Tie Node (TR_A side) | 2
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 53.2
Load Transferred (kW) | 3.22
TR_A Loading After (%) | 31
TR_B Loading After (%) | 40.6
Minimum Voltage (V) | 221.8