## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 54 | 8 | 51 | 19 | 29.9 | 20.63 | 50 | 39.6 | 3.1 | 11.9 | 35.6 | 226.4 | 187.8 | 187.8 | NO
| NG | 8 | 9 | 51 | 19 | 29.9 | 18.8 | 50 | 39.6 | 3.1 | 11.9 | 31.2 | 226.4 | 193.9 | 193.9 | NO
| NG | 9 | 11 | 51 | 19 | 29.9 | 8.27 | 50 | 39.6 | 3.1 | 18 | 26.7 | 225.3 | 200.6 | 200.6 | NO
| NG | 11 | 10 | 51 | 19 | 29.9 | 7.11 | 50 | 39.6 | 3.1 | 20.3 | 23.7 | 224.8 | 204.7 | 204.7 | NO
| NG | 10 | 29 | 51 | 19 | 29.9 | 7.11 | 50 | 39.6 | 3.1 | 20.5 | 23.7 | 224.8 | 204.7 | 204.7 | NO
| NG | 29 | 45 | 51 | 19 | 29.9 | 6.88 | 50 | 39.6 | 3.1 | 21.1 | 22.9 | 224.7 | 205.7 | 205.7 | NO
| NG | 45 | 22 | 51 | 19 | 29.9 | 6.88 | 50 | 39.6 | 3.1 | 21.1 | 22.5 | 224.7 | 206.2 | 206.2 | NO
1 | OK | 22 | 15 | 51 | 19 | 29.9 | 5.87 | 50 | 39.6 | 3.1 | 24.9 | 17.9 | 224 | 212 | 212 | YES
2 | OK | 15 | 41 | 51 | 19 | 29.9 | 5.05 | 50 | 39.6 | 3.1 | 26.6 | 16 | 223.6 | 214.4 | 214.4 | YES
3 | OK | 41 | 42 | 51 | 19 | 29.9 | 3.97 | 50 | 39.6 | 3.1 | 28.7 | 14.1 | 223.2 | 216.8 | 216.8 | YES
4 | ** OPTIMAL ** | 42 | 0 | 51 | 19 | 29.9 | 1.1 | 50 | 39.6 | 3.1 | 39 | 3.5 | 220.4 | 229.9 | 220.4 | YES
5 | OK | 0 | 34 | 51 | 19 | 29.9 | 1.1 | 50 | 39.6 | 3.1 | 39.2 | 3.5 | 220.3 | 229.9 | 220.3 | YES
6 | OK | 34 | 35 | 51 | 19 | 29.9 | 1.1 | 50 | 39.6 | 3.1 | 39.2 | 3.5 | 220.3 | 229.9 | 220.3 | YES
7 | OK | 35 | 36 | 51 | 19 | 29.9 | 1.04 | 50 | 39.6 | 3.1 | 39.5 | 3.2 | 220.2 | 230 | 220.2 | YES
8 | OK | 36 | 37 | 51 | 19 | 29.9 | 1.04 | 50 | 39.6 | 3.1 | 39.5 | 3.2 | 220.2 | 230 | 220.2 | YES
9 | OK | 37 | 70 | 51 | 19 | 29.9 | 1.04 | 50 | 39.6 | 3.1 | 39.5 | 3.2 | 220.2 | 230 | 220.2 | YES
10 | OK | 70 | 60 | 51 | 19 | 29.9 | 1.04 | 50 | 39.6 | 3.1 | 39.5 | 3.2 | 220.2 | 230 | 220.2 | YES
11 | OK | 60 | 50 | 51 | 19 | 29.9 | 1.04 | 50 | 39.6 | 3.1 | 39.5 | 3.2 | 220.2 | 230 | 220.2 | YES
12 | OK | 50 | 51 | 51 | 19 | 29.9 | 1.01 | 50 | 39.6 | 3.1 | 39.6 | 3.1 | 220.2 | 230.1 | 220.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 36-012323
TR_B (available) | 65-027559
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 39.6
TR_B Baseline Loading% | 3.1
Total Scenarios Evaluated | 19
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 42
Switch Child Node | 0
Tie Node (TR_A side) | 51
Tie Node (TR_B side) | 19
Tie Line Distance (m) | 29.9
Load Transferred (kW) | 1.1
TR_A Loading After (%) | 39
TR_B Loading After (%) | 3.5
Minimum Voltage (V) | 220.4