## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 20 | 10 | 23 | 35 | 65.7 | 13.96 | 50 | 92 | 31.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 10 | 9 | 23 | 35 | 65.7 | 13.57 | 50 | 92 | 31.4 | 60.3 | 35 | 217.9 | 212.9 | 212.9 | YES
2 | OK | 9 | 19 | 23 | 35 | 65.7 | 12.48 | 50 | 92 | 31.4 | 62.8 | 35 | 217.9 | 212.9 | 212.9 | YES
3 | OK | 19 | 17 | 23 | 35 | 65.7 | 11.83 | 50 | 92 | 31.4 | 64.2 | 35 | 217.9 | 212.9 | 212.9 | YES
4 | OK | 17 | 16 | 23 | 35 | 65.7 | 10.92 | 50 | 92 | 31.4 | 66.3 | 34.3 | 217.5 | 213.2 | 213.2 | YES
5 | OK | 16 | 15 | 23 | 35 | 65.7 | 10.35 | 50 | 92 | 31.4 | 67.6 | 33.9 | 217.2 | 213.4 | 213.4 | YES
6 | OK | 15 | 46 | 23 | 35 | 65.7 | 9.48 | 50 | 92 | 31.4 | 69.6 | 33.9 | 217.2 | 213.4 | 213.4 | YES
7 | OK | 46 | 26 | 23 | 35 | 65.7 | 9.48 | 50 | 92 | 31.4 | 69.6 | 33.9 | 217.2 | 213.4 | 213.4 | YES
8 | ** OPTIMAL ** | 26 | 2 | 23 | 35 | 65.7 | 7.09 | 50 | 92 | 31.4 | 75.2 | 32.7 | 216.4 | 213.9 | 213.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 36-014218
TR_B (available) | 58-016607
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 92
TR_B Baseline Loading% | 31.4
Total Scenarios Evaluated | 9
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 26
Switch Child Node | 2
Tie Node (TR_A side) | 23
Tie Node (TR_B side) | 35
Tie Line Distance (m) | 65.7
Load Transferred (kW) | 7.09
TR_A Loading After (%) | 75.2
TR_B Loading After (%) | 32.7
Minimum Voltage (V) | 213.9