## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 71 | 39 | 79 | 10 | 8.4 | 3.54 | 50 | 76.7 | 58.6 | 68.5 | 66.8 | 217.4 | 214.4 | 214.4 | YES
2 | OK | 39 | 40 | 79 | 10 | 8.4 | 0.01 | 50 | 76.7 | 58.6 | 76.6 | 58.6 | 217.2 | 216.4 | 216.4 | YES
3 | OK | 4 | 5 | 5 | 3 | 22.6 | 0.85 | 50 | 76.7 | 58.6 | 74.7 | 60.5 | 217.2 | 216.1 | 216.1 | YES
4 | OK | 13 | 14 | 6 | 15 | 4.3 | 4.98 | 50 | 76.7 | 58.6 | 65.2 | 70.3 | 218 | 215.3 | 215.3 | YES
| NG | 13 | 38 | 38 | 3 | 125.6 | 9.75 | 50 | 76.7 | 58.6 | 54.1 | 81.2 | 218.9 | 214.6 | 214.6 | NO
5 | OK | 14 | 12 | 6 | 15 | 4.3 | 3.69 | 50 | 76.7 | 58.6 | 65.2 | 67.2 | 218 | 215.2 | 215.2 | YES
| NG | 38 | 35 | 35 | 3 | 130.2 | 9.75 | 50 | 76.7 | 58.6 | 54.1 | 81.2 | 218.9 | 214.6 | 214.6 | NO
6 | OK | 12 | 11 | 6 | 15 | 4.3 | 3.69 | 50 | 76.7 | 58.6 | 68.1 | 67.2 | 217.8 | 215.2 | 215.2 | YES
7 | OK | 11 | 10 | 6 | 15 | 4.3 | 3.53 | 50 | 76.7 | 58.6 | 68.5 | 66.8 | 217.8 | 215.4 | 215.4 | YES
8 | OK | 10 | 70 | 6 | 15 | 4.3 | 3.33 | 50 | 76.7 | 58.6 | 69 | 66.4 | 217.8 | 215.3 | 215.3 | YES
9 | OK | 70 | 77 | 6 | 15 | 4.3 | 3.33 | 50 | 76.7 | 58.6 | 69 | 66.4 | 217.8 | 215.3 | 215.3 | YES
| NG | 41 | 24 | 19 | 0 | 52.5 | 10.47 | 50 | 76.7 | 58.6 | 52.1 | 83.2 | 223.2 | 215.3 | 215.3 | NO
10 | OK | 77 | 76 | 6 | 15 | 4.3 | 2.79 | 50 | 76.7 | 58.6 | 70.2 | 64.3 | 217.6 | 215.5 | 215.5 | YES
| NG | 24 | 23 | 19 | 0 | 52.5 | 9.91 | 50 | 76.7 | 58.6 | 53.4 | 81.8 | 223.2 | 215.2 | 215.2 | NO
11 | OK | 76 | 62 | 6 | 15 | 4.3 | 2.31 | 50 | 76.7 | 58.6 | 71.3 | 64 | 217.6 | 215.5 | 215.5 | YES
12 | OK | 23 | 25 | 19 | 0 | 52.5 | 3.45 | 50 | 76.7 | 58.6 | 68.5 | 66.5 | 218.6 | 216.2 | 216.2 | YES
13 | OK | 62 | 9 | 6 | 15 | 4.3 | 2.03 | 50 | 76.7 | 58.6 | 72 | 63.3 | 217.6 | 215.8 | 215.8 | YES
14 | OK | 62 | 63 | 63 | 3 | 94.5 | 0.28 | 50 | 76.7 | 58.6 | 76 | 59.2 | 217.2 | 216.3 | 216.3 | YES
15 | ** OPTIMAL ** | 25 | 26 | 19 | 0 | 52.5 | 3.06 | 50 | 76.7 | 58.6 | 69.4 | 65.6 | 218.7 | 216.4 | 216.4 | YES
16 | OK | 9 | 8 | 6 | 15 | 4.3 | 0.81 | 50 | 76.7 | 58.6 | 74.8 | 60.4 | 217.3 | 216.1 | 216.1 | YES
17 | OK | 26 | 57 | 19 | 0 | 52.5 | 1.15 | 50 | 76.7 | 58.6 | 73.9 | 61.2 | 217.1 | 216.4 | 216.4 | YES
18 | OK | 8 | 7 | 6 | 15 | 4.3 | 0.49 | 50 | 76.7 | 58.6 | 74.8 | 59.7 | 217.3 | 216.1 | 216.1 | YES
19 | OK | 57 | 20 | 19 | 0 | 52.5 | 1.15 | 50 | 76.7 | 58.6 | 73.9 | 61.2 | 217.1 | 216.4 | 216.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 36-019472
TR_B (available) | 34-000161
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 76.7
TR_B Baseline Loading% | 58.6
Total Scenarios Evaluated | 23
Feasible Scenarios | 19
--- Optimal Solution ---
Switch Parent Node | 25
Switch Child Node | 26
Tie Node (TR_A side) | 19
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 52.5
Load Transferred (kW) | 3.06
TR_A Loading After (%) | 69.4
TR_B Loading After (%) | 65.6
Minimum Voltage (V) | 216.4