## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 73 | 72 | 78 | 40 | 2.8 | 14.73 | 50 | 76.7 | 46.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 72 | 1 | 78 | 40 | 2.8 | 14.73 | 50 | 76.7 | 46.4 | 42.7 | 81 | 219.7 | 216.3 | 216.3 | NO
| NG | 1 | 0 | 78 | 40 | 2.8 | 14.73 | 50 | 76.7 | 46.4 | 42.7 | 81 | 219.7 | 216.3 | 216.3 | NO
| NG | 0 | 13 | 78 | 40 | 2.8 | 14.73 | 50 | 76.7 | 46.4 | 42.7 | 81 | 219.7 | 216.3 | 216.3 | NO
1 | OK | 13 | 38 | 78 | 40 | 2.8 | 9.75 | 50 | 76.7 | 46.4 | 54.1 | 69.1 | 218.9 | 220.1 | 218.9 | YES
2 | OK | 38 | 35 | 78 | 40 | 2.8 | 9.75 | 50 | 76.7 | 46.4 | 54.1 | 69.1 | 218.9 | 220.1 | 218.9 | YES
3 | OK | 35 | 34 | 78 | 40 | 2.8 | 9.14 | 50 | 76.7 | 46.4 | 55.5 | 67.6 | 218.9 | 220 | 218.9 | YES
4 | OK | 34 | 37 | 78 | 40 | 2.8 | 9.14 | 50 | 76.7 | 46.4 | 55.5 | 67.1 | 218.9 | 219.9 | 218.9 | YES
5 | OK | 37 | 33 | 78 | 40 | 2.8 | 8.9 | 50 | 76.7 | 46.4 | 56 | 67.1 | 218.9 | 219.9 | 218.9 | YES
6 | ** OPTIMAL ** | 33 | 32 | 78 | 40 | 2.8 | 8.9 | 50 | 76.7 | 46.4 | 56 | 67.1 | 218.9 | 219.9 | 218.9 | YES
7 | OK | 32 | 58 | 78 | 40 | 2.8 | 7.97 | 50 | 76.7 | 46.4 | 58.2 | 64.9 | 218.6 | 221 | 218.6 | YES
8 | OK | 58 | 74 | 78 | 40 | 2.8 | 7.27 | 50 | 76.7 | 46.4 | 59.8 | 63.2 | 218.6 | 220.8 | 218.6 | YES
9 | OK | 74 | 46 | 78 | 40 | 2.8 | 2.98 | 50 | 76.7 | 46.4 | 69.7 | 53.3 | 217.7 | 222.9 | 217.7 | YES
10 | OK | 46 | 47 | 78 | 40 | 2.8 | 2.98 | 50 | 76.7 | 46.4 | 69.7 | 53.3 | 217.7 | 222.9 | 217.7 | YES
11 | OK | 47 | 48 | 48 | 40 | 18.5 | 2.98 | 50 | 76.7 | 46.4 | 69.7 | 53.3 | 217.7 | 222.9 | 217.7 | YES
12 | OK | 48 | 16 | 16 | 40 | 31.7 | 2.2 | 50 | 76.7 | 46.4 | 71.5 | 51.5 | 217.3 | 223.3 | 217.3 | YES
13 | OK | 16 | 15 | 15 | 40 | 89 | 1.27 | 50 | 76.7 | 46.4 | 73.7 | 49.3 | 217.2 | 223.4 | 217.2 | YES
14 | OK | 15 | 18 | 18 | 40 | 113.5 | 0.37 | 50 | 76.7 | 46.4 | 75.8 | 47.3 | 217.2 | 223.4 | 217.2 | YES
15 | OK | 18 | 17 | 17 | 40 | 146.3 | 0.37 | 50 | 76.7 | 46.4 | 75.8 | 47.3 | 217.2 | 223.4 | 217.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 36-019472
TR_B (available) | 66-018426
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 76.7
TR_B Baseline Loading% | 46.4
Total Scenarios Evaluated | 19
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 33
Switch Child Node | 32
Tie Node (TR_A side) | 78
Tie Node (TR_B side) | 40
Tie Line Distance (m) | 2.8
Load Transferred (kW) | 8.9
TR_A Loading After (%) | 56
TR_B Loading After (%) | 67.1
Minimum Voltage (V) | 218.9