## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 63 | 64 | 76 | 16 | 42.8 | 17.54 | 50 | 89.1 | 10.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 64 | 9 | 76 | 16 | 42.8 | 16.87 | 50 | 89.1 | 10.7 | 49.4 | 38.2 | 212 | 198.3 | 198.3 | NO
| NG | 9 | 10 | 76 | 16 | 42.8 | 16.33 | 50 | 89.1 | 10.7 | 50.7 | 38.2 | 212 | 198.3 | 198.3 | NO
| NG | 10 | 11 | 76 | 16 | 42.8 | 13.45 | 50 | 89.1 | 10.7 | 57.3 | 31.6 | 211.3 | 205.1 | 205.1 | NO
| NG | 11 | 12 | 76 | 16 | 42.8 | 12.26 | 50 | 89.1 | 10.7 | 60 | 31.6 | 211.3 | 205.1 | 205.1 | NO
| NG | 12 | 13 | 76 | 16 | 42.8 | 11.99 | 50 | 89.1 | 10.7 | 60.6 | 30.4 | 211.1 | 206.3 | 206.3 | NO
| NG | 13 | 14 | 76 | 16 | 42.8 | 11.41 | 50 | 89.1 | 10.7 | 62 | 30.4 | 211.1 | 206.3 | 206.3 | NO
| NG | 14 | 15 | 76 | 16 | 42.8 | 10.89 | 50 | 89.1 | 10.7 | 63.2 | 29.6 | 211 | 207 | 207 | NO
| NG | 15 | 16 | 76 | 16 | 42.8 | 10.68 | 50 | 89.1 | 10.7 | 63.7 | 29.6 | 211 | 207 | 207 | NO
| NG | 16 | 17 | 76 | 16 | 42.8 | 10.68 | 50 | 89.1 | 10.7 | 63.7 | 29.6 | 211 | 207 | 207 | NO
| NG | 17 | 53 | 76 | 16 | 42.8 | 9.95 | 50 | 89.1 | 10.7 | 65.3 | 29.6 | 211 | 207 | 207 | NO
| NG | 53 | 18 | 76 | 16 | 42.8 | 8.54 | 50 | 89.1 | 10.7 | 68.7 | 29.6 | 211 | 207 | 207 | NO
| NG | 18 | 19 | 76 | 16 | 42.8 | 8.53 | 50 | 89.1 | 10.7 | 68.7 | 29.6 | 211 | 207 | 207 | NO
| NG | 19 | 20 | 76 | 16 | 42.8 | 7.71 | 50 | 89.1 | 10.7 | 70.6 | 29.6 | 211 | 207 | 207 | NO
1 | ** OPTIMAL ** | 20 | 57 | 76 | 16 | 42.8 | 6.53 | 50 | 89.1 | 10.7 | 70.6 | 25.4 | 211 | 211.1 | 211 | YES
2 | OK | 57 | 68 | 76 | 16 | 42.8 | 6.53 | 50 | 89.1 | 10.7 | 73.4 | 25.4 | 210.5 | 211.1 | 210.5 | YES
3 | OK | 68 | 74 | 76 | 16 | 42.8 | 6.26 | 50 | 89.1 | 10.7 | 74 | 24.2 | 210.4 | 212.2 | 210.4 | YES
4 | OK | 74 | 29 | 29 | 16 | 126.3 | 6.26 | 50 | 89.1 | 10.7 | 74 | 24.2 | 210.4 | 212.4 | 210.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 36-019494
TR_B (available) | 62-000639
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 89.1
TR_B Baseline Loading% | 10.7
Total Scenarios Evaluated | 18
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 20
Switch Child Node | 57
Tie Node (TR_A side) | 76
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 42.8
Load Transferred (kW) | 6.53
TR_A Loading After (%) | 70.6
TR_B Loading After (%) | 25.4
Minimum Voltage (V) | 211