## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 63 | 62 | 27 | 0 | 47.8 | 20.4 | 50 | 89.1 | 0 | 41.1 | 41.4 | 215.1 | 214.1 | 214.1 | YES
2 | OK | 62 | 61 | 27 | 0 | 47.8 | 20.4 | 50 | 89.1 | 0 | 41.1 | 41.4 | 215.1 | 214.1 | 214.1 | YES
| NG | 61 | 59 | 27 | 0 | 47.8 | 19.62 | 50 | 89.1 | 0 | 42.9 |  | 215.1 | 5.1681e+58 | 215.1 | NO
3 | OK | 59 | 58 | 27 | 0 | 47.8 | 18.81 | 50 | 89.1 | 0 | 44.8 | 41.4 | 215.1 | 214.1 | 214.1 | YES
4 | OK | 58 | 60 | 27 | 0 | 47.8 | 18.47 | 50 | 89.1 | 0 | 45.5 | 41.4 | 215.1 | 214.1 | 214.1 | YES
5 | ** OPTIMAL ** | 60 | 8 | 27 | 0 | 47.8 | 18.16 | 50 | 89.1 | 0 | 46.3 | 40.1 | 214.9 | 214.5 | 214.5 | YES
6 | OK | 8 | 7 | 27 | 0 | 47.8 | 11.94 | 50 | 89.1 | 0 | 60.6 | 32.1 | 214 | 217.4 | 214 | YES
7 | OK | 8 | 41 | 67 | 3 | 142.6 | 6.22 | 50 | 89.1 | 0 | 74.6 | 7.6 | 210.3 | 227.4 | 210.3 | YES
8 | OK | 7 | 6 | 27 | 0 | 47.8 | 10.53 | 50 | 89.1 | 0 | 63.8 | 32.1 | 214 | 217.4 | 214 | YES
9 | OK | 41 | 46 | 67 | 3 | 142.6 | 5.58 | 50 | 89.1 | 0 | 76.1 | 7.6 | 210.3 | 227.4 | 210.3 | YES
10 | OK | 6 | 73 | 27 | 0 | 47.8 | 9.53 | 50 | 89.1 | 0 | 66.2 | 32.1 | 214 | 217.4 | 214 | YES
11 | OK | 46 | 47 | 67 | 3 | 142.6 | 5.58 | 50 | 89.1 | 0 | 76.1 | 7.6 | 210.3 | 227.4 | 210.3 | YES
12 | OK | 73 | 5 | 27 | 0 | 47.8 | 9.42 | 50 | 89.1 | 0 | 66.4 | 32.1 | 214 | 217.4 | 214 | YES
13 | OK | 5 | 4 | 27 | 0 | 47.8 | 8.68 | 50 | 89.1 | 0 | 68.1 | 32.1 | 214 | 217.4 | 214 | YES
14 | OK | 4 | 2 | 27 | 0 | 47.8 | 8.22 | 50 | 89.1 | 0 | 69.2 | 32.1 | 214 | 217.4 | 214 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 36-019494
TR_B (available) | 67-036344
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 89.1
TR_B Baseline Loading% | 0
Total Scenarios Evaluated | 15
Feasible Scenarios | 14
--- Optimal Solution ---
Switch Parent Node | 60
Switch Child Node | 8
Tie Node (TR_A side) | 27
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 47.8
Load Transferred (kW) | 18.16
TR_A Loading After (%) | 46.3
TR_B Loading After (%) | 40.1
Minimum Voltage (V) | 214.5