## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 13 | 27 | 73 | 34 | 1.7 | 0.8 | 50 | 82.5 | 61.4 | 77.4 | 64.5 | 216.2 | 217.8 | 216.2 | YES
2 | OK | 13 | 42 | 42 | 34 | 75.5 | 1.81 | 50 | 82.5 | 61.4 | 75.5 | 68.5 | 217.5 | 216.4 | 216.4 | YES
3 | OK | 27 | 45 | 73 | 34 | 1.7 | 0.8 | 50 | 82.5 | 61.4 | 79.4 | 64.5 | 215.6 | 217.8 | 215.6 | YES
4 | ** OPTIMAL ** | 42 | 37 | 37 | 34 | 79.3 | 1.63 | 50 | 82.5 | 61.4 | 76.2 | 67.8 | 217.3 | 216.6 | 216.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 37-002367
TR_B (available) | 45-023785
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.5
TR_B Baseline Loading% | 61.4
Total Scenarios Evaluated | 4
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 42
Switch Child Node | 37
Tie Node (TR_A side) | 37
Tie Node (TR_B side) | 34
Tie Line Distance (m) | 79.3
Load Transferred (kW) | 1.63
TR_A Loading After (%) | 76.2
TR_B Loading After (%) | 67.8
Minimum Voltage (V) | 216.6